SECTION 01 91 13

GENERAL COMMISSIONING REQUIREMENTS

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

General requirements for coordinating and scheduling commissioning.

Commissioning Team duties

Commissioning meetings.

Commissioning scheduling.

Test equipment, instrumentation, and tools for commissioning.

Construction verification.

Functional performance testing.

Commissioning tests and commissioning test demonstration.

Commissioning Report.

Related Requirements:

Section 01 33 00 "Submittal Procedures" for submittal procedure requirements for commissioning.

Section 01 77 00 "Closeout Procedures" for Certificate of Construction-Phase Commissioning Completion submittal requirements.

Section 01 78 23 "Operation and Maintenance Data" for preliminary operation and maintenance (O&M) data submittal requirements.

Section 26 08 00 "Commissioning of Electrical Systems" for technical  commissioning requirements for electrical systems.

DEFINITIONS

Acceptance Criteria: Threshold of acceptable work quality or performance specified for a Commissioning activity, including Pre-Functional Checklists, Functional Performance Tests, performance test demonstrations, Commissioning tests, and Commissioning test demonstrations.

Commissioning: A quality-focused process for verifying and documenting that facility and all of its systems and assemblies are planned, designed, installed, and tested to comply with project requirements. Requirements specified here are limited to construction phase Commissioning activities. Scope of Commissioning process is defined in Section 01 10 00 "Summary."

Commissioning Agent:  A District appointed entity that plans and coordinates all activities that implement commissioning as outlined by District’s Basis of Design.

Commissioning Plan: A document, prepared by Commissioning Agent, that outlines the organization, schedule, allocation of resources, and documentation requirements of  commissioning.

Commissioning Report:  A document, prepared by the Commissioning Agent, that records the activities and results of the Commissioning process.

Commissioning: The process of ensuring that systems are designed, installed, functionally tested and performing in conformity with the District’s Requirements and that the District has received complete equipment/systems documentation and training.

Construction Verification:  A quality control verification process performed by the  installer as building assemblies, components, equipment and systems are being  installed that documents that the materials, installation procedures, interfaces with other trades, start-up, testing and operations are correct, complete, in compliance with  Contract Documents and manufacturer’s recommendations and are ready for Functional Performance Testing.

District's Project Requirements: A narrative of the program, use and functional requirements of the building with a description of the Project goals and criteria in general categories (e.g.: flexibility of use, ease of maintenance, future expansion, etc.) and specific categories (e.g.: specialized environments, specific sustainable features, quality of materials, etc.).

Functional Performance Tests: Contractor testing of installed building assemblies, components, equipment, systems and interfaces which confirms correct performance through all operating modes and compliance with Contract Documents, manufacturer’s recommendations and the District’s Project Requirements.

Retro-Commissioning: A systematic process for improving and optimizing a building’s operations and supporting those improvements with enhanced documentation and operator training.

Test: Performance tests, performance test demonstrations, commissioning tests, and commissioning test demonstrations.

ABBREVIATIONS

The following abbreviations are used in this Section:

A/E     Architect / Engineer.

BAS: Building Automation System.

Cx:  Commissioning.

CxA: Commissioning Agent.

DPR: District’s Project Requirements.

FPT: Functional Performance Tests.

O&M: Operations and Maintenance.

PI:  Project Inspector.

PPO:   Physical Plant Operations

P/T: Pressure / Temperature.

TAB: Testing, Adjusting, and Balancing

COMMISSIONING TEAM DUTIES

INFORMATIONAL SUBMITTALS

Comply with requirements in Section 01 33 00 "Submittal Procedures" for submittal procedure general requirements for Commissioning process.

Commissioning Plan Information:

List of Contractor-appointed Commissioning team members to include specific personnel and subcontractors performing various Commissioning requirements.

Contractor personnel and subcontractors participating in each test.

List of instrumentation required for each test to include identification of parties that will provide instrumentation for each test.

Commissioning schedule, including two-week look-ahead Commissioning schedules as specified in Part 3.

List test instrumentation, equipment, and monitoring devices. Include:

Make, model, serial number, and application for each instrument, equipment, and monitoring device.

Brief description of intended use.

Calibration record showing:

Calibration agency, including name and contact information.

Last date of calibration.

Range of values for which calibration is valid.

Certification of accuracy.

Certification for calibration equipment traceable to NIST.

Due date of next calibration.

Test Reports:

Pre-Startup Report: Prior to startup of equipment or a system, submit completed PFCs.

Test Data Reports: At end of each day in which tests are conducted, submit test data for tests performed.

Commissioning Issue Reports: Daily, at end of each day in which tests are conducted, submit Commissioning issue reports for tests for which acceptable results were not achieved.

Weekly Progress Report: Weekly, at end of each week in which tests are conducted, submit a progress report.

Data Trend Logs: Submit data trend logs at end of trend log period.

PFCs:

Material checks.

Installation checks.

Startup procedures, where required.

CLOSEOUT SUBMITTALS

Commissioning Report:

At Construction-Phase Commissioning Completion, include:

Pre-startup reports.

PFCs completed and signed.

FPTs completed and signed.

Progress reports.

Commissioning issue report log.

Commissioning Tracking Matrix.

Meeting Minutes.

Test & Balance Reports.

Commissioning issue reports showing resolution of issues.

Correspondence or other documents related to resolution of issues.

Agreed upon plan for resolution of open issues.

Other reports required by Commissioning process.

List unresolved issues and reasons they remain unresolved and should be exempted from requirements for Construction-Phase Commissioning Completion.

Report shall include Commissioning work of Contractor.

Request for Certificate of Construction-Phase Commissioning Process Completion.

O&M Data: For proprietary test equipment, instrumentation, and tools to include in O&M manuals.

PRODUCTS

TEST EQUIPMENT, INSTRUMENTATION, AND TOOLS

Test equipment and instrumentation required to perform Commissioning process shall remain property of Contractor unless otherwise indicated.

Test equipment and instrumentation required to perform Commissioning process shall comply with:

Be manufactured for purpose of testing and measuring tests for which they are being used and have an accuracy to test and measure system performance within tolerances required to determine acceptable performance.

Calibrated and certified.

Calibration performed and documented by a qualified calibration agency according to national standards applicable to tools and instrumentation being calibrated. Calibration shall be current according to national standards or within test equipment and instrumentation manufacturer's recommended intervals, whichever is more frequent, but not less than within six months of initial use on Project. Calibration tags shall be permanently affixed.

Repair and recalibrate test equipment and instrumentation if dismantled, dropped, or damaged since last calibrated.

Maintain test equipment and instrumentation.

Use test equipment and instrumentation only for testing or monitoring Work for which they are designed.

PROPRIETARY TEST EQUIPMENT, INSTRUMENTATION, AND TOOLS

Proprietary test equipment, instrumentation, and tools are those manufactured or prescribed by tested equipment manufacturer and required for work on its equipment as a condition of equipment warranty, or as otherwise required to service, repair, adjust, calibrate, or perform work on its equipment.

Identify proprietary test equipment, instrumentation, and tools required in test equipment identification list submittal.

REPORT FORMAT AND ORGANIZATION

General Format and Organization:

Record report on USB thumb drive.

Electronic Data: Portable document format (PDF); a single file with outline-organized bookmarks for major and minor tabs and tab contents itemized for specific reports.

Commissioning Report:

Include a table of contents and an index to each test.

Include major tabs for each specification section.

Include minor tabs for each test.

Within each minor tab, include:

Test specification.

Pre-startup reports.

Test data forms, PFCs completed and signed.

FPTs completed and signed.

Commissioning issue reports, showing resolution of issues, and documentation related to resolution of issues pertaining to a single test. Group data forms, Commissioning issue reports showing resolution of issues, and documentation related to resolution of issues for each test repetition together within minor tab, in reverse chronological order (most recent on top).

EXECUTION

PREPARATION

Review preliminary PFCs and preliminary FPT procedures and data forms.

PRE-FUNCTIONAL CHECKLISTS (PFCs)

Checklists-Functional Checklists cannot modify or conflict with Contract Documents.

Create PFCs based on actual systems and equipment to be included in Project.

Material Checks: Compare specified characteristics and approved submittals with materials as received. Include factory tests and other evaluations, adjustments, and tests performed prior to shipment if applicable.

Service connection requirements, including configuration, size, location, and other pertinent characteristics.

Included optional features.

Inspect and record physical condition of materials and equipment, including agreement with approved submittals, cleanliness, and lack of damage.

Installation Checks:

Location according to Drawings and approved Shop Drawings.

Configuration.

Compliance with manufacturers' written installation instructions.

Attachment to structure.

Access clearance to allow for maintenance, service, repair, removal, and replacement without need to disassemble or remove other equipment or building elements. Access coordinated with other building elements and equipment, including ceiling and wall access panels, in a manner consistent with OSHA fall-protection regulations and safe work practices.

Utility connections are of correct characteristics, as applicable.

Correct labeling and identification.

Startup Checks: Verify readiness of equipment to be energized. Include manufacturer's standard startup procedures and forms.

Startup: Perform and document initial operation of equipment to prove that it is installed properly and operates as intended according to manufacturer's standard startup procedures, at minimum. Use of manufacturer provided start-up form is acceptable.

Deferred PFCs: Obtain District approval of proposed deferral of PFCs, including proposed schedule of completion of each deferred PFC, before submitting request for Certificate of Construction-Phase Commissioning Process Completion. When approved, deferred PFCs may be completed after date of Construction-Phase Commissioning Completion. Include in request for Certificate of Construction-Phase Commissioning Process Completion:

Identify deferred  PFCs by number and title.

Provide a target schedule for completion of deferred  PFCs.

Written approval of proposed deferred  PFCs , including approved schedule of completion of each deferred PFC.

Delayed PFCs: Obtain District approval of proposed delayed PFCs, including proposed schedule of completion of each delayed PFC, before submitting request for Certificate of Construction-Phase Commissioning Process Completion. When approved, delayed  PFCs may be completed after date of Construction-Phase Commissioning Completion. Include in request for Certificate of Construction-Phase Commissioning Process Completion:

Identify delayed  PFC by  PFC number and title.

Provide a target schedule for completion of delayed PFCs.

Written approval of proposed delayed  PFCs, including approved schedule of completion of each delayed  PFC.

GENERAL EXECUTION REQUIREMENTS

Schedule and coordinate Commissioning process with Contractor’s accepted Construction Schedule.

Perform activities identified in  PFCs including tests, and document results of actions as construction proceeds.

Perform test demonstrations for District Commissioning Agent. Unless otherwise indicated, demonstrate tests for 100 percent of work to which test applies.

Report test data and Commissioning issue resolutions.

Schedule personnel to participate in and perform Commissioning process work.

COMMISSIONING  TESTING

Quality Control: PFCs, including FPTs, are quality-control tools designed to improve functional quality of Project. Test demonstrations evaluate effectiveness of Contractor's quality-control process.

Commissioning Agent will be present to witness Commissioning work requiring signature of a District witness, including test demonstrations.

Provide sufficient notice, regarding their completion schedule for PFCs and startup of all equipment and systems to allow FPTs to be scheduled. Commissioning team shall oversee, witness, and document performance all equipment and systems. Commissioning Agent in association with contractor/subcontractors and facility staff shall execute tests. FPTs shall be conducted after PFCs, and startup has been satisfactorily completed.  Control system shall be sufficiently tested and approved by Commissioning Agent before it is used, to verify performance of other components or systems.  Air balancing and water balancing shall be completed before FPTs of air or water-related equipment or systems.  Testing proceeds from components to sub-systems to systems.  When proper performance of all interacting individual systems has been achieved, interface or coordinated responses between systems shall be checked.

Pre-Functional Checklists (PFCs):

Complete PFCs as Work is completed.

Distribute  PFCs to installing contractors before they start work.

Installers:

Verify installation using approved  Pre-Functional Checklist as Work is completed.

Complete and sign PFC as work is completed on a weekly  basis for work performed during preceding week.

Installation Compliance Issues: Record as an installation compliance issue work found to be incomplete, inaccessible, at variance with Contract Documents, nonfunctional, or that does not comply with PFCs. Record installation compliance issues on PFC at time they are identified. Record corrective action and how future Work should be modified before signing off PFC.

Pre-Startup Audit: Prior to executing startup procedures, review completed installation checks to determine readiness for startup and operation. Report conditions, which, if left uncorrected, adversely impact ability of systems or equipment to operate satisfactorily or to comply with acceptance criteria. Prepare pre-startup report for each system.

FPT Procedures and Test Data Forms:

Test procedures shall define step-by-step procedures to be used to execute FPTs and test demonstrations.

Test procedures shall be specific to make, model, and application of equipment and systems being tested.

Completed test data forms are official records of test results.

Commissioning Agent will provide to Contractor preliminary PFCs and FPT Procedures after approval of Product Data, Shop Drawings, and preliminary O&M manual.

Review preliminary test procedures and test data forms, and provide comments within 14 days of receipt from Commissioning Agent. Review shall address:

Equipment protection and warranty issues, including manufacturers' installation and startup recommendations, and O&M instructions.

Applicability of procedure to specific software, equipment, and systems approved for installation.

After Contractor has reviewed and commented on preliminary test procedures and test data forms, Commissioning Agent will revise and reissue approved revised test procedures and test data forms marked "Approved for Testing."

Use only approved test procedures and test data forms marked "Approved for Testing" to perform and document tests and test demonstrations.

Performance of Tests:

Sampling Rates

Tests: 100 percent.

Test demonstrations: 100 percent, unless otherwise indicated.

Perform and complete each step of approved test procedures in order listed.

Record data observed during performance of tests on approved data forms at time of test performance and when results are observed.

Record test results that are not within range of acceptable results on Commissioning issue report forms in addition to recording results on approved test procedures and data forms according to "Commissioning Compliance Issues" Paragraph in this Article.

On completion of a test, sign completed test procedure and data form. Tests for which test procedures and data forms are incomplete, not signed, or which indicate performance that does not comply with acceptance criteria will be rejected. Tests for which test procedures and data forms are rejected shall be repeated and results resubmitted.

Perform tests on a sample of tests after test data submittals are approved.

Sampling rate for tests: 100 percent, unless otherwise indicated in individual test specification.

Notify District witness at least three days in advance of each test.

Perform and complete each step of approved test procedures in order listed.

Record data observed during performance of test on approved data forms at time of test and when results are observed.

Provide full access to District witness to directly observe performance of all aspects of system response during test. On completion of a test, sign completed data form and obtain signature of District witness at time of test to authenticate reported results.

Test data forms not signed by Contractor and District witness at time of completion of procedure will be rejected. Test for which data forms are rejected shall be repeated and results shall be resubmitted.

False load test requirements are specified in related sections.

Where false load testing is specified, provide temporary equipment, power, controls, wiring, piping, valves, and other necessary equipment and connections required to apply specified load to system. False load system shall be capable of steady-state operation and modulation at level of load specified.

Deferred Tests:

Deferred Test List: Identify, in request for Certificate of Construction-Phase Commissioning Process Completion, proposed deferred tests or other tests approved for deferral until specified seasonal or other conditions are available. When approved, deferred tests may be completed after date of Construction-Phase Commissioning Completion. Identify proposed deferred tests in request for Certificate of Construction-Phase Commissioning Process Completion as follows:

Identify deferred tests by number and title.

Provide a target schedule for completion of deferred tests.

Schedule and coordinate deferred tests. Schedule deferred tests when specified conditions are available. Notify District Construction Manager, Architect and Commissioning Agent at least three working days (minimum) in advance of tests.

Where deferred tests are specified, coordinate participation of necessary personnel and of Architect, Commissioning Agent, and District witness. Schedule deferred tests to minimize occupant and facility impact. Obtain Architect's approval of proposed schedule.

Commissioning  Compliance Issues:

Test results that are not within range of acceptable results are Commissioning compliance issues.

Track and report Commissioning compliance issues until resolution and retesting are successfully completed.

If a test fails, determine cause of failure. Direct timely resolution of issue and then repeat demonstration. If a test demonstration must be repeated due to failure caused by Contractor work or materials, reimburse District for billed costs for participation in repeated demonstration.

Test Results: If a test demonstration fails to meet acceptance criteria, perform the following:

Complete a Commissioning compliance issue report form promptly on discovery of test results that do not comply with acceptance criteria.

Submit Commissioning compliance issue report form within 72 hours of test.

Determine cause of failure.

Establish responsibility for corrective action if failure is due to conditions found to be Contractor's responsibility.

Commissioning Compliance Issue Report: Provide a Commissioning compliance issue report for each issue. Do not report multiple issues on same Commissioning compliance issue report.

Exception: If an entire class of devices is determined to exhibit identical issue, they may be reported on a single Commissioning compliance issue report. (For example, if all return-air damper actuators that are specified to fail to open position are found to fail to closed position, they may be reported on a single Commissioning issue report. If a single Commissioning issue report is used for multiple Commissioning compliance issues, each device shall be identified in report, and total number of devices at issue shall be identified.

Complete and submit Part 1 of Commissioning compliance issue report immediately when condition is observed.

Record Commissioning compliance issue report number and describe deficient condition on data form.

Resolve Commissioning compliance issues promptly. Complete and submit Part 2 of Commissioning compliance issue report when issues are resolved.

Diagnose and correct failed test as follows:

Perform diagnostic tests and activities required to determine fundamental cause of issues observed.

Record each step of diagnostic procedure prior to performing procedure. Update written procedure as changes become necessary.

Record results of each step of diagnostic procedure.

Record conclusion of diagnostic procedure on fundamental cause of issue.

Determine and record corrective measures.

Include diagnosis of fundamental cause of issues in Commissioning compliance issue report.

Retest:

Schedule and repeat complete test procedure for each test demonstration for which acceptable results are not achieved. Obtain signature of District witness on retest data forms. Repeat test demonstration until acceptable results are achieved. Except for issues that are determined to result from design errors or omissions, or other conditions beyond Contractor's responsibility, compensate District for direct costs incurred as result of repeated test demonstrations to achieve acceptable results.

For each repeated test demonstration, submit a new test data form, marked "Retest."

Do not correct Commissioning compliance issues during test.

Exceptions will be allowed if cause of issue is obvious and resolution can be completed in a reasonable amount time. If corrections are made under this exception, note deficient conditions on test data form and issue a Commissioning compliance issue report. A new test data form, marked "Retest," shall be initiated after resolution has been completed.

SEQUENCING

Sequencing of Commissioning Verification Activities: For a particular material, item of equipment, assembly, or system, perform following in order listed unless otherwise indicated:

Pre-Functional Checklists (PFCs):

Material checks.

Installation checks.

Startup, as appropriate. Some startup may depend on component performance. Such startup may follow component performance tests on which startup depends.

Performance Tests:

Static tests, as appropriate.

Component performance tests. Some component performance tests may depend on completion of startup. Such component performance tests may follow startup.

Equipment and assembly performance tests.

System performance tests.

Functional Performance Tests.

Before performing FPTs, verify that materials, equipment, assemblies, and systems are delivered, installed, started, and adjusted to perform according to PFCs.

Verify readiness of materials, equipment, assemblies, and systems by performing tests prior to performing FPT demonstrations. Notify Construction Manager if acceptable results cannot be achieved due to conditions beyond Contractor's control or responsibility.

Commence FPTs as soon as installation checks for materials, equipment, assemblies, or systems are satisfactorily completed. Tests of a particular system may proceed prior to completion of other systems, provided incomplete work does not interfere with successful execution of test.

SCHEDULING

Commence Commissioning process as early in construction period as possible.

Commissioning Schedule: Integrate Commissioning activities into Contractor’s accepted Construction Schedule.

Include detailed Commissioning activities in monthly updated Construction Schedule and short-interval schedule submittals.

Schedule start date and duration for following Commissioning activities:

Submittals.

Preliminary O&M manual submittals.

Installation checks.

Startup, where required.

FPTs.

Schedule shall include a line item for each installation check, startup, and test activity specific to equipment or systems involved.

Determine milestones and prerequisites for Commissioning process. Show Commissioning milestones, prerequisites, and dependencies in monthly updated critical-path-method construction schedule and short-interval schedule submittals

Provide estimated date of construction-phase Commissioning process completion.

COMMISSIONING REPORT

- Commissioning Agent will provide Contractor, Architect, and District a Commissioning Report for the Project upon Substantial Completion.  This report will include contact information for key members of the commissioning team; description of commissioned systems, commissioning activities, sampling protocol and results.   The report will also include the District’s Project Requirements, Basis-of-Design, Construction Verification Checklist Tracking Report, and Functional Performance Test Tracking Report.

END OF SECTION 01 91 13

San Diego Unified School District Guide Specifications

Document Version: February 14, 2022 Bulletin