MasterSpec 2015

SECTION 07 41 13.16

STANDING-SEAM METAL ROOF PANELS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes standing-seam metal roof panels.

PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

Preinstallation Conference: Conduct conference at Project site.

If needed, insert list of conference participants not mentioned in Section 01 31 00 "Project Management and Coordination."

Retain subparagraphs below if additional requirements are necessary; revise to include more specific information about conference.

Meet with District District Construction Manager, Project Inspector, Architect, metal panel Installer, metal panel manufacturer's representative, structural-support Installer, and installers whose work interfaces with or affects metal panels, including installers of roof accessories and roof-mounted equipment.

Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

Review methods and procedures related to metal panel installation, including manufacturer's written instructions.

Examine support conditions for compliance with requirements, including alignment between and attachment to structural members.

Review structural loading limitations of [deck] [purlins and rafters] during and after roofing.

Review flashings, special details, drainage, penetrations, equipment curbs, and condition of other construction that affect metal panels.

Review governing regulations, certificates, and tests and inspections if applicable.

Review temporary protection requirements for metal panel systems during and after installation.

Review procedures for repair of metal panels damaged after installation.

Document proceedings, including corrective measures and actions required, and furnish copy of record to each participant.

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each type of panel and accessory.

Shop Drawings:

Include fabrication and installation layouts of metal panels; details of edge conditions, joints, panel profiles, corners, anchorages, attachment system, trim, flashings, closures, and accessories; and special details.

Accessories: Include details of the flashing, trim, and anchorage systems, at a scale of not less than 1-1/2 inches per 12 inches.

Samples for Verification: For each type of exposed finish required, prepared on Samples of size indicated below.

Metal Panels: 12 inches long by actual panel width. Include clips, fasteners, closures, and other metal panel accessories.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in "Quality Assurance" Article.

Qualification Data: For Installer.

Product Test Reports: For each product, for tests performed by a qualified testing agency.

Field quality-control reports.

Manufacturer Certificates: Signed by roofing manufacturer certifying that standing seam metal roof system complies with requirements specified in "Performance Requirements" Article.

Submit evidence of compliance with performance requirements.

Sample Warranties: For special warranties.

CLOSEOUT SUBMITTALS

Maintenance Data: For metal panels to include in maintenance manuals.

Information Card:  Furnish a typewritten card, laminated in plastic.  Card shall be 8 1/2-by-11 inches and shall contain the information listed on Form 1 located at end of this section.

QUALITY ASSURANCE

Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer.

Retain "UL-Certified, Portable Roll-Forming Equipment" Paragraph below if portable roll-forming equipment is allowed for on-site roll forming.

UL-Certified, Portable Roll-Forming Equipment: UL-certified, portable roll-forming equipment capable of producing metal panels warranted by manufacturer to be the same as factory-formed products. Maintain UL certification of portable roll-forming equipment for duration of work.

Retain “Mockups” paragraph below if needed for verification of system.

DELIVERY, STORAGE, AND HANDLING

Deliver components, metal panels, and other manufactured items so as not to be damaged or deformed. Package metal panels for protection during transportation and handling.

Unload, store, and erect metal panels in a manner to prevent bending, warping, twisting, and surface damage.

Stack metal panels horizontally on platforms or pallets, covered with suitable weathertight and ventilated covering. Store metal panels to ensure dryness, with positive slope for drainage of water. Do not store metal panels in contact with other materials that might cause staining, denting, or other surface damage.

Retain strippable protective covering on metal panels during installation.

FIELD CONDITIONS

Weather Limitations: Proceed with installation only when existing and forecasted weather conditions permit assembly of metal panels to be performed according to manufacturers' written instructions and warranty requirements.

COORDINATION

Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

Coordinate metal panel installation with rain drainage work, flashing, trim, construction of soffits, and other adjoining work to provide a leakproof, secure, and noncorrosive installation.

WARRANTY

Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of metal panel systems that fail in materials or workmanship within specified warranty period.

Failures include:

Structural failures including rupturing, cracking, or puncturing.

Deterioration of metals and other materials beyond normal weathering.

Warranty Period:  Two years from date of Substantial Completion.

Special Warranty on Panel Finishes: Manufacturer's standard form in which manufacturer agrees to repair finish or replace metal panels that show evidence of deterioration of factory-applied finishes within specified warranty period.

Exposed Panel Finish: Deterioration includes:

Color fading more than 5 Hunter units when tested according to ASTM D 2244.

Chalking in excess of a No. 8 rating when tested according to ASTM D 4214.

Cracking, checking, peeling, or failure of paint to adhere to bare metal.

Finish Warranty Period:  20 years from date of Substantial Completion.

Special Weathertightness Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace standing-seam metal roof panel assemblies that fail to remain weathertight, including leaks, within specified warranty period.

Warranty Period: Five years from date of Substantial Completion.

PRODUCTS

PERFORMANCE REQUIREMENTS

Retain one of two "Energy Performance" Paragraphs below for roofs that must comply with the California Energy Code.  Values shown in the first paragraph are those required for low-slope roofs by prescriptive approach.  Values shown in second paragraph are those required for steep slope roofs by prescriptive approach.  Revise if other values are required for building-envelope trade-off approach or whole-building performance approach. A list of products tested according to CRRC-1 with their test values is available in PDF at www.coolroofs.org.

Energy Performance: Roofing system shall have a minimum aged solar reflectance of 0.65 and a minimum thermal emittance of 0.75 or a minimum solar reflectance index (SRI) of 75 when tested according to CRRC-1.

Energy Performance:  Roofing system shall have a minimum aged solar reflectance of 0.20 and a minimum thermal emittance of 0.75 or a minimum solar reflectance index (SRI) of 16 when tested according to CRRC-1.

Structural Performance: Provide metal panel systems capable of withstanding the effects of the following loads, based on testing according to ASTM E 1592:

Wind Loads: As indicated on Drawings.

Other Design Loads: As indicated on Drawings.

Retain "Air Infiltration" and "Water Penetration under Static Pressure" paragraphs below for single-skin metal panels that span openings between supports; usually delete for panels mounted on solid substrates.

Air Infiltration: Air leakage of not more than 0.06 cfm/sq. ft. when tested according to ASTM E 1680 at the following test-pressure difference:

Value in first option in "Test-Pressure Difference" Subparagraph below is equivalent to a 25-mph wind and is ASTM E 1680 default. Products tested to value in second option below, equivalent to a 50-mph wind, are widely available. Revise to suit Project.

Test-Pressure Difference: 1.57 lbf/sq. ft.

Water Penetration under Static Pressure: No water penetration when tested according to ASTM E 1646 at the following test-pressure difference:

Value in first option in "Test-Pressure Difference" Subparagraph below is equivalent to a 34-mph wind and is ASTM E 1646 default. Products tested to value in second option below, equivalent to a 50-mph wind, are widely available. Revise to suit Project.

Test-Pressure Difference: 2.86 lbf/sq. ft.

Test in "Hydrostatic-Head Resistance" Paragraph below is for resistance to hydrostatic pressure from standing water. Retain only for panels capable of watertight (hydrostatic) installation, not for panels used in water-shedding (hydrokinetic) installations that rely on underlayment for watertightness.

Hydrostatic-Head Resistance: No water penetration when tested according to ASTM E 2140.

UL listings include requirements for the entire assembly and not solely the metal roof panels.  Verify roof structure complies with the rating.

Wind-Uplift Resistance: Provide metal roof panel assemblies that comply with UL 580 for wind-uplift-resistance class indicated.

Uplift Rating:  UL 90.

Thermal Movements: Allow for thermal movements from ambient and surface temperature changes by preventing buckling, opening of joints, overstressing of components, failure of joint sealants, failure of connections, and other detrimental effects. Base calculations on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Temperature Change (Range):  120 deg F, ambient; 180 deg F, material surfaces.

STANDING-SEAM METAL ROOF PANELS

General: Provide factory-formed metal roof panels designed to be installed by lapping and interconnecting raised side edges of adjacent panels with joint type indicated and mechanically attaching panels to supports using concealed clips in side laps. Include clips, cleats, pressure plates, and accessories required for weathertight installation.

Steel Panel Systems: Unless more stringent requirements are indicated, comply with ASTM E 1514.

Aluminum Panel Systems: Unless more stringent requirements are indicated, comply with ASTM E 1637.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

Vertical-Rib, Snap-Joint, Standing-Seam Metal Roof Panels: Formed with vertical ribs at panel edges and intermediate stiffening ribs symmetrically spaced ribs; designed for sequential installation by mechanically attaching panels to supports using concealed clips located under one side of panels, engaging opposite edge of adjacent panels, and snapping panels together.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

AEP Span; A BlueScope Steel Company.

Berridge Manufacturing Company.

Metal Sales Manufacturing Corporation.

Or Equal.

Metallic-Coated Steel Sheet: Zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

Nominal Thickness: 0.028-inch.

Exterior Finish:  Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Aluminum Sheet: Coil-coated sheet, ASTM B 209, alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

Thickness: 0.032-inch.

Surface: Smooth, flat finish.

Exterior Finish: Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Clips: One-piece fixed to accommodate thermal movement.

Retain one of two "Material" subparagraphs below. Retain steel clips for metallic-coated steel roof panels and stainless-steel clips for aluminum panels.

Material: 0.028-inch- nominal thickness, zinc-coated (galvanized) or aluminum-zinc alloy-coated steel sheet.

Material: 0.025-inch- thick, stainless-steel sheet.

Panel Coverage: 16 inches.

Panel Height: 1.5 inches.

Vertical-Rib, Seamed-Joint, Standing-Seam Metal Roof Panels: Formed with vertical ribs at panel edges and intermediate stiffening ribs symmetrically spaced between ribs; designed for sequential installation by mechanically attaching panels to supports using concealed clips located under one side of panels, engaging opposite edge of adjacent panels, and mechanically seaming panels together.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

AEP Span; A BlueScope Steel Company.

Berridge Manufacturing Company.

Metal Sales Manufacturing Corporation.

Or Equal.

Metallic-Coated Steel Sheet: Zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

Nominal Thickness: 0.028-inch.

Exterior Finish:  Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Aluminum Sheet: Coil-coated sheet, ASTM B 209, alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

Thickness: 0.032-inch.

Surface: Smooth, flat finish.

Exterior Finish: Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Clips: One-piece fixed to accommodate thermal movement.

Material: 0.028-inch- nominal thickness, zinc-coated (galvanized) or aluminum-zinc alloy-coated steel sheet.

Material: 0.025-inch- thick, stainless-steel sheet.

Joint Type: As standard with manufacturer.

Panel Coverage: 16 inches.

Panel Height: 1.5 inches.

Trapezoidal-Rib, Snap-Joint, Standing-Seam Metal Roof: Formed with raised trapezoidal ribs at panel edges and intermediate stiffening ribs symmetrically spaced between ribs; designed for sequential installation by mechanically attaching panels to supports using concealed clips located under one side of panels, engaging opposite edge of adjacent panels, and snapping panels together.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

AEP Span; A BlueScope Steel Company.

MBCI; a division of NCI Group, Inc.

McElroy Metal, Inc.

Or Equal.

Metallic-Coated Steel Sheet: Zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

Nominal Thickness: 0.028-inch.

Exterior Finish:  Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Aluminum Sheet: Coil-coated sheet, ASTM B 209, alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

Thickness: 0.032-inch.

Surface: Smooth, flat finish.

Exterior Finish: Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Clips: One-piece fixed to accommodate thermal movement.

Material: 0.028-inch- nominal thickness, zinc-coated (galvanized) or aluminum-zinc alloy-coated steel sheet.

Material: 0.025-inch- thick, stainless-steel sheet.

Panel Coverage: 16 inches.

Panel Height: 1.5 inches.

Trapezoidal-Rib, Seamed-Joint, Standing-Seam Metal Roof Panels: Formed with raised trapezoidal ribs at panel edges and intermediate stiffening ribs symmetrically spaced between ribs; designed for sequential installation by mechanically attaching panels to supports using concealed clips located under one side of panels, engaging opposite edge of adjacent panels, and mechanically seaming panels together.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

MBCI; a division of NCI Group, Inc.

Metal Sales Manufacturing Corporation.

Morin - A Kingspan Group Company.

Or Equal.

Metallic-Coated Steel Sheet: Zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

Nominal Thickness: 0.028-inch.

Exterior Finish:  Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations Aluminum Sheet: Coil-coated sheet, ASTM B 209, alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

Thickness: 0.032-inch.

Surface: Smooth, flat finish.

Exterior Finish: Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Clips: One-piece fixed to accommodate thermal movement.

Material: 0.028-inch- nominal thickness, zinc-coated (galvanized) or aluminum-zinc alloy-coated steel sheet.

Material: 0.025-inch- thick, stainless-steel sheet.

Joint Type: As standard with manufacturer.

Panel Coverage: 16 inches.

Panel Height: 1.5 inches.

Integral-Standing-Seam Metal Roof Panels: Formed with integral ribs at panel edges and intermediate stiffening ribs symmetrically spaced between ribs; designed for sequential installation by mechanically attaching panels to supports using concealed clips located under one side of panels and lapping and interconnecting side edges of adjacent panels.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ATAS International, Inc.

McElroy Metal, Inc.

Or Equal.

Metallic-Coated Steel Sheet: Zinc-coated (galvanized) steel sheet complying with ASTM A 653/A 653M, G90 coating designation, or aluminum-zinc alloy-coated steel sheet complying with ASTM A 792/A 792M, Class AZ50 coating designation; structural quality. Prepainted by the coil-coating process to comply with ASTM A 755/A 755M.

Nominal Thickness: 0.028-inch.

Exterior Finish:  Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations.

Aluminum Sheet: Coil-coated sheet, ASTM B 209, alloy as standard with manufacturer, with temper as required to suit forming operations and structural performance required.

Thickness: 0.032-inch.

Surface: Smooth, flat finish.

Exterior Finish: Two-coat fluoropolymer.

Color: As indicated by manufacturer's designations

Clips: One-piece fixed to accommodate thermal movement.

Material: 0.028-inch- nominal thickness, zinc-coated (galvanized) or aluminum-zinc alloy-coated steel sheet.

Material: 0.025-inch- thick, stainless-steel sheet.

Panel Coverage: 16 inches.

Panel Height: [1.0-inch] [1.5 inches] [2.0 inches] <Insert dimension>.

UNDERLAYMENT MATERIALS

Retain appropriate paragraphs in this article for metal roof panels applied over sheathing.

Underlayments listed in "Self-Adhering, High-Temperature Underlayment" Paragraph below are suitable for higher temperatures associated with metal roofing.

Self-Adhering, High-Temperature Underlayment: Provide self-adhering, cold-applied, sheet underlayment, a minimum of 30 mils thick, consisting of slip-resistant, polyethylene-film top surface laminated to a layer of butyl or SBS-modified asphalt adhesive, with release-paper backing. Provide primer when recommended by underlayment manufacturer.

Thermal Stability: Stable after testing at 240 deg F; ASTM D 1970.

Low-Temperature Flexibility: Passes after testing at minus 20 deg F; ASTM D 1970.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Carlisle Residential; a division of Carlisle Construction Materials.

Grace Construction Products; W.R. Grace & Co. -- Conn.

Henry Company.

Or Equal.

Sheet in "Slip Sheet" Paragraph below is used to separate metal roof panels from underlayment. Retain if required.

Slip Sheet: Manufacturer's recommended slip sheet, of type required for application.

MISCELLANEOUS MATERIALS

Miscellaneous Metal Subframing and Furring: ASTM C 645; cold-formed, metallic-coated steel sheet, ASTM A 653/A 653M, G90 coating designation or ASTM A 792/A 792M, Class AZ50 coating designation unless otherwise indicated. Provide manufacturer's standard sections as required for support and alignment of metal panel system.

Retain panel accessories, flashing, and trim as required and coordinate with those specified in Section 07 62 00 "Sheet Metal Flashing and Trim."

Panel Accessories: Provide components required for a complete, weathertight panel system including trim, copings, fasciae, mullions, sills, corner units, clips, flashings, sealants, gaskets, fillers, closure strips, and similar items. Match material and finish of metal panels unless otherwise indicated.

Closures: Provide closures at eaves and ridges, fabricated of same metal as metal panels.

Backing Plates: Provide metal backing plates at panel end splices, fabricated from material recommended by manufacturer.

Closure Strips: Closed-cell, expanded, cellular, rubber or crosslinked, polyolefin-foam or closed-cell laminated polyethylene; minimum 1-inch-thick, flexible closure strips; cut or premolded to match metal panel profile. Provide closure strips where indicated or necessary to ensure weathertight construction.

Flashing and Trim: Provide flashing and trim formed from same material as metal panels as required to seal against weather and to provide finished appearance. Locations include eaves, rakes, corners, bases, framed openings, ridges, fasciae, and fillers. Finish flashing and trim with same finish system as adjacent metal panels.

If required, insert special requirements for ridge closures, corner units, copings, fasciae, and fillers.

Gutters: Formed from same material as roof panels, complete with end pieces, outlet tubes, and other special pieces as required. Fabricate in minimum 96-inch-long sections, of size and metal thickness according to SMACNA's "Architectural Sheet Metal Manual." Furnish gutter supports spaced a maximum of 36 inches o.c., fabricated from same metal as gutters. Provide wire ball strainers of compatible metal at outlets. Finish gutters to match [metal roof panels] [roof fascia and rake trim].

Limit use of sheet metal downspouts to areas not subject to vandalism such as from higher roof to lower roof.  Specify downspouts subject to vandalism in Section 22 14 13 “Facility Storm Drainage Piping.”

Downspouts: Formed from same material as roof panels. Fabricate in 10-foot-long sections, complete with formed elbows and offsets, of size and metal thickness according to SMACNA's "Architectural Sheet Metal Manual." Finish downspouts to match gutters.

Roof Curbs: Fabricated from same material as roof panels, [0.048-inch] <Insert dimension> nominal thickness; with bottom of skirt profiled to match roof panel profiles and with welded top box and integral full-length cricket. Fabricate curb subframing of 0.060-inch-nominal thickness, angle-, C-, or Z-shaped steel sheet. Fabricate curb and subframing to withstand indicated loads of size and height indicated. Finish roof curbs to match metal roof panels.

Insulate roof curb with 1-inch-thick, rigid insulation.

Panel Fasteners: Self-tapping screws designed to withstand design loads.

Panel Sealants: Provide sealant type recommended by manufacturer that are compatible with panel materials, are nonstaining, and do not damage panel finish.

Sealant Tape: Pressure-sensitive, 100 percent solids, gray polyisobutylene compound sealant tape with release-paper backing. Provide permanently elastic, nonsag, nontoxic, nonstaining tape 1/2-inch wide and 1/8-inch thick.

Joint Sealant: ASTM C 920; elastomeric polyurethane or silicone sealant; of type, grade, class, and use classifications required to seal joints in metal panels and remain weathertight; and as recommended in writing by metal panel manufacturer.

Butyl-Rubber-Based, Solvent-Release Sealant: ASTM C 1311.

FABRICATION

General: Fabricate and finish metal panels and accessories at the factory, by manufacturer's standard procedures and processes, as necessary to fulfill indicated performance requirements demonstrated by laboratory testing. Comply with indicated profiles and with dimensional and structural requirements.

Retain "On-Site Fabrication" Paragraph below to permit use of on-site, portable roll-forming equipment.

On-Site Fabrication: Subject to compliance with requirements of this Section, metal panels may be fabricated on-site using UL-certified, portable roll-forming equipment if panels are of same profile and warranted by manufacturer to be equal to factory-formed panels. Fabricate according to equipment manufacturer's written instructions and to comply with details shown.

Provide panel profile, including major ribs and intermediate stiffening ribs, if any, for full length of panel.

Retain first paragraph below if gaskets or sealants are factory installed.

Fabricate metal panel joints with factory-installed captive gaskets or separator strips that provide a weathertight seal and prevent metal-to-metal contact, and that minimize noise from movements.

Sheet Metal Flashing and Trim: Fabricate flashing and trim to comply with manufacturer's recommendations and recommendations in SMACNA's "Architectural Sheet Metal Manual" that apply to design, dimensions, metal, and other characteristics of item indicated.

Form exposed sheet metal accessories that are without excessive oil canning, buckling, and tool marks and that are true to line and levels indicated, with exposed edges folded back to form hems.

Seams for Aluminum: Fabricate nonmoving seams with flat-lock seams. Form seams and seal with epoxy seam sealer. Rivet joints for additional strength.

Seams for Other Than Aluminum: Fabricate nonmoving seams in accessories with flat-lock seams. Tin edges to be seamed, form seams, and solder.

Sealed Joints: Form nonexpansion, but movable, joints in metal to accommodate sealant and to comply with SMACNA standards.

Conceal fasteners and expansion provisions where possible. Exposed fasteners are not allowed on faces of accessories exposed to view.

Fabricate cleats and attachment devices from same material as accessory being anchored or from compatible, noncorrosive metal recommended in writing by metal panel manufacturer.

Size: As recommended by SMACNA's "Architectural Sheet Metal Manual" or metal panel manufacturer for application, but not less than thickness of metal being secured.

FINISHES

Protect mechanical and painted finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

Appearance of Finished Work: Variations in appearance of abutting or adjacent pieces are acceptable if they are within one-half of the range of approved Samples. Noticeable variations in same piece are unacceptable. Variations in appearance of other components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

Steel Panels and Accessories:

Two-Coat Fluoropolymer: AAMA 621. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in color coat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

Concealed Finish: Apply pretreatment and manufacturer's standard white or light-colored acrylic or polyester backer finish consisting of prime coat and wash coat with a minimum total dry film thickness of 0.5-mil.

Aluminum Panels and Accessories:

Retain one of first two subparagraphs below.

Two-Coat Fluoropolymer: AAMA 2605. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in color coat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

Three-Coat Fluoropolymer: AAMA 2605. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in both color coat and clear topcoat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances, metal panel supports, and other conditions affecting performance of the Work.

Retain one or both subparagraphs below.

Examine primary and secondary roof framing to verify that rafters, purlins, angles, channels, and other structural panel support members and anchorages have been installed within alignment tolerances required by metal roof panel manufacturer.

Examine solid roof sheathing to verify that sheathing joints are supported by framing or blocking and that installation is within flatness tolerances required by metal roof panel manufacturer.

Retain subparagraph below with subparagraph above for systems that depend on air- or water-resistive barriers to prevent air infiltration or water penetration.

Verify that air- or water-resistive barriers have been installed over sheathing or backing substrate to prevent air infiltration or water penetration.

Examine roughing-in for components and systems penetrating metal panels to verify actual locations of penetrations relative to seam locations of metal panels before installation.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Miscellaneous Supports: Install subframing, furring, and other miscellaneous panel support members and anchorages according to ASTM C 754 and metal panel manufacturer's written recommendations.

UNDERLAYMENT INSTALLATION

Retain this article for metal roof panels applied over solid roof sheathing.

Self-Adhering Sheet Underlayment: Apply primer if required by manufacturer. Comply with temperature restrictions of underlayment manufacturer for installation. Apply at locations indicated [below] [on Drawings], wrinkle free, in shingle fashion to shed water, and with end laps of not less than 6 inches staggered 24 inches between courses. Overlap side edges not less than 3-1/2 inches.[ Extend underlayment into gutter trough.] Roll laps with roller. Cover underlayment within 14 days.

Retain subparagraph below or delete if indicated on Drawings.

Apply over the entire roof surface.

Retain "Slip Sheet" Paragraph below if required.

Slip Sheet: Apply slip sheet over underlayment before installing metal roof panels.

Flashings: Install flashings to cover underlayment to comply with requirements specified in Section 07 62 00 "Sheet Metal Flashing and Trim."

METAL PANEL INSTALLATION

General: Install metal panels according to manufacturer's written instructions in orientation, sizes, and locations indicated. Install panels perpendicular to supports unless otherwise indicated. Anchor metal panels and other components of the Work securely in place, with provisions for thermal and structural movement.

Shim or otherwise plumb substrates receiving metal panels.

Flash and seal metal panels at perimeter of all openings. Fasten with self-tapping screws. Do not begin installation until air- or water-resistive barriers and flashings that will be concealed by metal panels are installed.

Install screw fasteners in predrilled holes.

Locate and space fastenings in uniform vertical and horizontal alignment.

Install flashing and trim as metal panel work proceeds.

Locate panel splices over, but not attached to, structural supports. Stagger panel splices and end laps to avoid a four-panel lap splice condition.

Align bottoms of metal panels and fasten with blind rivets, bolts, or self-tapping screws. Fasten flashings and trim around openings and similar elements with self-tapping screws.

Provide weathertight escutcheons for pipe- and conduit-penetrating panels.

Fasteners:

Steel Panels: Use stainless-steel fasteners for surfaces exposed to the exterior; use galvanized-steel fasteners for surfaces exposed to the interior.

Aluminum Panels: Use aluminum or stainless-steel fasteners for surfaces exposed to the exterior; use aluminum or galvanized-steel fasteners for surfaces exposed to the interior.

Anchor Clips: Anchor metal roof panels and other components of the Work securely in place, using manufacturer's approved fasteners according to manufacturers' written instructions.

Metal Protection: Where dissimilar metals contact each other or corrosive substrates, protect against galvanic action as recommended in writing by metal panel manufacturer.

Indicate on the drawings the point of fixity.

Standing-Seam Metal Roof Panel Installation: Fasten metal roof panels to supports with concealed clips at each standing-seam joint at location, spacing, and with fasteners recommended in writing by manufacturer and as indicated on Drawings.

Install clips to supports with self-tapping fasteners.

Install pressure plates at locations indicated in manufacturer's written installation instructions.

Retain "Snap Joint" or "Seamed Joint" Subparagraph below; coordinate with products selected in Part 2.

Snap Joint: Nest standing seams and fasten together by interlocking and completely engaging factory-applied sealant.

Seamed Joint: Crimp standing seams with manufacturer-approved, motorized seamer tool so clip, metal roof panel, and factory-applied sealant are completely engaged.

Retain "Watertight Installation" Subparagraph below for hydrostatic (watertight) panel installation; delete if not required.

Watertight Installation:

Apply a continuous ribbon of sealant or tape to seal joints of metal panels, using sealant or tape as recommend in writing by manufacturer as needed to make panels watertight.

Provide sealant or tape between panels and protruding equipment, vents, and accessories.

At panel splices, nest panels with minimum 6-inch end lap, sealed with sealant and fastened together by interlocking clamping plates.

Accessory Installation: Install accessories with positive anchorage to building and weathertight mounting, and provide for thermal expansion. Coordinate installation with flashings and other components.

Install components required for a complete metal panel system including trim, copings, corners, seam covers, flashings, sealants, gaskets, fillers, closure strips, and similar items. Provide types indicated by metal roof panel manufacturers; or, if not indicated, types recommended by metal roof panel manufacturer.

Flashing and Trim: Comply with performance requirements, manufacturer's written installation instructions, and SMACNA's "Architectural Sheet Metal Manual." Provide concealed fasteners where possible, and set units true to line and level as indicated. Install work with laps, joints, and seams that will be permanently watertight and weather resistant.

Install exposed flashing and trim that is without buckling and tool marks, and that is true to line and levels indicated, with exposed edges folded back to form hems. Install sheet metal flashing and trim to fit substrates and achieve waterproof and weather-resistant performance.

Expansion Provisions: Provide for thermal expansion of exposed flashing and trim. Space movement joints at a maximum of 10 feet with no joints allowed within 24 inches of corner or intersection. Where lapped expansion provisions cannot be used or would not be sufficiently weather resistant and waterproof, form expansion joints of intermeshing hooked flanges, not less than 1-inch deep, filled with mastic sealant (concealed within joints).

Gutters: Join sections with riveted and soldered or lapped and sealed joints. Attach gutters to eave with gutter hangers spaced not more than 36 inches o.c. using manufacturer's standard fasteners. Provide end closures and seal watertight with sealant. Provide for thermal expansion.

Downspouts: Join sections with telescoping joints. Provide fasteners designed to hold downspouts securely 1-inch away from walls; locate fasteners at top and bottom and at approximately 60 inches o.c. in between.

Retain one of two subparagraphs below.

Provide elbows at base of downspouts to direct water away from building.

Connect downspouts to underground drainage system indicated.

Roof Curbs: Install flashing around bases where they meet metal roof panels.

FIELD QUALITY CONTROL

Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect metal roof panel installation, including accessories. Report results in writing.

Remove and replace applications of metal roof panels where tests and inspections indicate that they do not comply with specified requirements.

Additional tests and inspections, at Contractor's expense, are performed to determine compliance of replaced or additional work with specified requirements.

Prepare test and inspection reports.

CLEANING AND PROTECTION

Remove temporary protective coverings and strippable films, if any, as metal panels are installed, unless otherwise indicated in manufacturer's written installation instructions. On completion of metal panel installation, clean finished surfaces as recommended by metal panel manufacturer. Maintain in a clean condition during construction.

Replace metal panels that have been damaged or have deteriorated beyond successful repair by finish touchup or similar minor repair procedures.

END OF SECTION 07 41 13.16

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021

FORM 1 – ROOFING SYSTEM DESCRIPTION

1.	Location:________________________________	2.Bldg. Name:	___________________

3.	Bldg. No.:__________4.Roof Area (SF):_________5.	Contract No.:__________________

6.	Deck Slope:_______________________

7.	Type of Deck:

( )	Metal								( )	Wood Plank or Plywood

( )	Cast-In-Place Concrete				( )	Other:__________________________________

( )	Precast/Prestressed Concrete

8.	Type of Insulation Board:

( )	Polyisocyanurate/Composite		( )	Polyisocyanurate

( )	Polystyrene/Composite				( )	Polystyrene

( )	Perlite								( )	Mineral Fiber

( )	Other:_______________________________________

9.	Insulation Manufacturer:________________________________________________________

10.	Insulation Thickness:________________________

11.	Roofing Type:

( ) Built-Up (Asphalt)					( )	PVC

( ) Metal								( )	SBS Mod. Bitumen

( ) Shingles								( )	Other:__________________________________

12.	Roofing Manufacturer:_________________________________________________________

13.	Roofing Installer/Warrantor:_____________________________________________________

14.	Roofing Application Method:

( )	Bitumen							( )	Fully Adhered

( )	Mechanically Fastened 				( )	Mechanically Fastened/Fully Adhered

( )	Other:_______________________________________

15.	Warranty Period:	From: _______________________To:____________________________

16.	Warranty Serial Number:_______________________________________________________

17.	Date Roofing Completed:__________________18.Inspector:__________________________

19.	Prime Contractor Name/Address:_________________________________________________

Signature:_________________________________________Date:__________________________

INSTRUCTIONS FOR FORM 1 (Do Not Post)

1.	Location:	Name of facility as shown on contract.

2.	Bldg. Name:	As shown on contract or as provided by District Construction Manager.

3.	Bldg. Number:	As provided by District Construction Manager.

4.	Roof Area:	Area in square feet of roof for which deck insulation, membrane, etc. are the same.  A separate form is required if any part of roof system is different over other areas of the roof.

5.	Contract Number:	As shown on the contract.

6.	Show deck slope.

7.	Deck:  Check appropriate block.

8.	Type of Insulation Board:	Check appropriate block.

9.	Show manufacturer of insulation.

10.	Show minimum thickness of installed insulation.

11.	Roofing Type:	Check appropriate block.

12.	Show roofing manufacturer's name.

13.	Roofing Installer's or Contractor's name.

14.	Roofing Application Method:  Check appropriate block.

15.	Warranty Period:	Insert start and end dates.

16.	Warranty Serial Number:	Insert serial number.

17.	Show date of Substantial Completion.	Warranty period begins on this date.

18.	Show Project Inspector's name.

19.	Prime Contractor Name/Address/Signature:	Must be signed and dated by an official of Contracting firm.