MasterSpec 2014

SECTION 07 84 43

JOINT FIRESTOPPING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Joints in or between fire-resistance-rated constructions.

Joints at exterior curtain-wall / floor intersections.

Joints in smoke barriers.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 07 84 13 "Penetration Firestopping" for penetrations in fire-resistance-rated walls, horizontal assemblies, and smoke barriers wall identification.

Section 09 22 16 "Non-Structural Metal Framing" for firestop tracks for metal-framed partition heads.

PRE-INSTALLATION MEETINGS

Retain "Pre-installation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

Pre-installation Conference: Conduct conference at Project site.

If needed, insert list of conference participants not mentioned in Section 01 31 00 "Project Management and Coordination."

ACTION SUBMITTALS

Product Data: For each type of product.

Product Schedule: For each joint firestopping system. Include location, description of joint type, illustration of firestopping system, and design designation of qualified testing agency.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in "Quality Assurance" Article.

Qualification Data: For Installer.

Product Test Reports: For each joint firestopping system, for tests performed by a qualified testing agency.

CLOSEOUT SUBMITTALS

Installer Certificates: From Installer indicating that joint firestopping systems have been installed in compliance with requirements and manufacturer's written instructions.

QUALITY ASSURANCE

Verify that installers are available to perform work in Project location. A list of FM Approvals-approved firestop contractors may be found on www.fmapprovals.com, and a list of UL-qualified firestop contractors may be found on www.ul.com/contractor. A list of firestop contractors who are approved or qualified and are also members of Firestop Contractors International Association may be found at www.fcia.org.

Installer Qualifications: A firm that has been approved by FM Approval according to FM Approval 4991, "Approval Standard for Firestop Contractors," or been evaluated by UL and found to comply with its "Qualified Firestop Contractor Program Requirements", or been trained and certified by firestopping manufacturer.

PROJECT CONDITIONS

Environmental Limitations: Do not install joint firestopping systems when ambient or substrate temperatures are outside limits permitted by joint firestopping system manufacturers or when substrates are wet due to rain, frost, condensation, or other causes.

Install and cure joint firestopping systems per manufacturer's written instructions using natural means of ventilation or, where this is inadequate, forced-air circulation.

COORDINATION

Coordinate construction of joints to ensure that joint firestopping systems can be installed according to specified firestopping system design.

Coordinate sizing of joints to accommodate joint firestopping systems.

PRODUCTS

PERFORMANCE REQUIREMENTS

Fire-Test-Response Characteristics:

Perform joint firestopping system tests by a qualified testing agency acceptable to authorities having jurisdiction.

Test per testing standards referenced in "Joint Firestopping Systems" Article. Provide rated systems complying with the following requirements:

Joint firestopping systems shall bear classification marking of a qualified testing agency.

UL in its "Fire Resistance Directory."

JOINT FIRESTOPPING SYSTEMS

Joint Firestopping Systems: Systems that resist spread of fire, passage of smoke and other gases, and maintain original fire-resistance rating of assemblies in or between which joint firestopping systems are installed. Joint firestopping systems shall accommodate building movements without impairing their ability to resist the passage of fire and hot gases.

Joints in or between Fire-Resistance-Rated Construction: Provide joint firestopping systems with ratings determined per ASTM E 1966 or UL 2079.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3M Fire Protection Products.

Hilti, Inc.

Tremco, Inc.

Or Equal.

Fire-Resistance Rating: Equal to or exceeding the fire-resistance rating of the wall, floor, or roof in or between which it is installed.

Retain "Joints at Exterior Curtain-Wall / Floor Intersections" Paragraph below if exterior curtain-wall / floor intersections are included in Project and indicate locations on Drawings. Coordinate with the Joint Firestopping System Schedule.

Joints at Exterior Curtain-Wall / Floor Intersections: Provide joint firestopping systems with rating determined per ASTM E 2307.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3M Fire Protection Products.

Hilti, Inc.

Tremco, Inc.

Or Equal.

F-Rating: Equal to or exceeding the fire-resistance rating of the floor assembly.

Retain "Joints in Smoke Barriers" Paragraph below if smoke barriers are included in Project and indicate locations on Drawings. Coordinate with the Joint Firestopping System Schedule.

Joints in Smoke Barriers: Provide fire-resistive joint systems with ratings determined per UL 2079 based on testing at a positive pressure differential of 0.30-inch wg.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3M Fire Protection Products.

Hilti, Inc.

Tremco, Inc.

Or Equal.

Rating in "L-Rating" Subparagraph below indicates resistance to air leakage.

L-Rating: Not exceeding 5.0 cfm/ft. of joint at both ambient and elevated temperatures.

Exposed Joint Firestopping Systems: Flame-spread and smoke-developed indexes of less than 25 and 450, respectively, as determined per ASTM E 84.

Accessories: Provide components of fire-resistive joint systems, including primers and forming materials, that are needed to install elastomeric fill materials and to maintain ratings required. Use only components specified by joint firestopping system manufacturer and approved by the qualified testing agency for conditions indicated.

EXECUTION

EXAMINATION

Examine substrates and conditions, with Installer present, for compliance with requirements for joint configurations, substrates, and other conditions affecting performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Surface Cleaning:  Clean joints immediately before installing fire-resistive joint systems.  Comply with fire-resistive joint system manufacturer's written instructions and the following requirements:

Remove from surfaces of joint substrates foreign materials that could interfere with adhesion of elastomeric fill materials or compromise fire-resistive rating.

Clean joint substrates to produce clean, sound surfaces capable of developing optimum bond with elastomeric fill materials. Remove loose particles remaining from cleaning operation.

Remove laitance and form-release agents from concrete.

Retain paragraph below if products selected require priming.

Prime substrates where recommended in writing by joint firestopping system manufacturer using that manufacturer's recommended products and methods. Confine primers to areas of bond; do not allow spillage and migration onto exposed surfaces.

INSTALLATION

General: Install fire-resistive joint systems to comply with manufacturer's written installation instructions and published drawings for products and applications indicated.

Install forming / damming / backing materials and other accessories of types required to support elastomeric fill materials during their application and in position needed to produce cross-sectional shapes and depths required to achieve fire ratings indicated.

After installing elastomeric fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not indicated as permanent components of fire-resistive joint system.

Install elastomeric fill materials for fire-resistive joint systems by proven techniques to produce the following results:

Elastomeric fill voids and cavities formed by joints and forming materials as required to achieve fire-resistance ratings indicated.

Apply elastomeric fill materials so they contact and adhere to substrates formed by joints.

For elastomeric fill materials that will remain exposed after completing the Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

FIELD QUALITY CONTROL

Inspection:  The Project Inspector will inspect all joint firestopping.

Where deficiencies are found or joint firestopping systems are damaged or removed due to testing, repair or replace joint firestopping systems so they comply with requirements.

Proceed with enclosing joint firestopping systems with other construction only after inspection has been completed and installation approved by the Project Inspector.

CLEANING AND PROTECTION

Clean off excess elastomeric fill materials adjacent to joints as the Work progresses by methods and with cleaning materials that are approved in writing by joint firestopping system manufacturers and that do not damage materials in which joints occur.

Provide final protection and maintain conditions during and after installation that ensure joint firestopping systems are without damage or deterioration at time of Substantial Completion. If damage or deterioration occurs despite such protection, cut out and remove damaged or deteriorated fire-resistive joint systems immediately and install new materials to produce fire-resistive joint systems complying with specified requirements.

END OF SECTION 07 84 43

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021