MasterSpec 2013

SECTION 10 44 13

FIRE PROTECTION CABINETS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Fire-protection cabinets for the following:

Portable fire extinguishers.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 10 44 16 "Fire Extinguishers."

PRE-INSTALLATION CONFERENCE

Retain "Pre-installation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a pre-installation conference.

Pre-installation Conference: Conduct conference at Project site.

Retain subparagraph below if additional requirements are necessary; include information about conference.

Review methods and procedures related to fire-protection cabinets, including:

Schedules and coordination requirements.

ACTION SUBMITTALS

Product Data:  For each type of product. Show door hardware, cabinet type, trim style, and panel style. Include roughing-in dimensions and details showing recessed, semirecessed, or surface-mounting method and relationships of box and trim to surrounding construction.

Shop Drawings:  For fire-protection cabinets. Include plans, elevations, sections, details, and attachments to other work.

Retain "Samples" Paragraph below with a subordinate list if applicable.

Samples:  For each type of exposed finish required.

Product Schedule:  For fire-protection cabinets. Show metal finish and features for each unit. Coordinate final fire-protection cabinet schedule with fire-extinguisher schedule to ensure proper fit and function. Use same designations indicated on Drawings.

CLOSEOUT SUBMITTALS

Maintenance Data:  For fire-protection cabinets to include in maintenance manuals.

COORDINATION

Consider retaining this article if fire-protection cabinets are specified by series only or for complex projects.

Coordinate size of fire-protection cabinets to ensure that type and capacity of fire extinguishers indicated are accommodated.

Requirement in paragraph below applies only to recessed and semi-recessed cabinets.

Coordinate sizes and locations of fire-protection cabinets with wall depths.

PRODUCTS

PERFORMANCE REQUIREMENTS

Requirement in "Fire-Rated Fire-Protection Cabinets" Paragraph below applies only to recessed and semirecessed cabinets that are installed in fire-rated walls.

Fire-Rated Fire-Protection Cabinets: Listed and labeled to comply with requirements in ASTM E 814 for fire-resistance rating of walls where they are installed.

FIRE-PROTECTION CABINET

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

Cabinet Type:  Suitable for fire extinguisher.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

JL Industries, Inc.; a division of the Activar Construction Products Group.

Larsens Manufacturing Company.

Potter Roemer LLC.

Or Equal.

Second and third options in "Cabinet Construction" Paragraph below are available only for recessed and semirecessed cabinets.

Cabinet Construction: Nonrated or 1-hour fire rated, as indicated on Drawings.

Retain "Fire-Rated Cabinets" Subparagraph below for fire-rated cabinets. Revise below if required.

Fire-Rated Cabinets:  Construct fire-rated cabinets with double walls fabricated from 0.043-inch-thick cold-rolled steel sheet lined with minimum 5/8-inch-thick fire-barrier material. Provide factory-drilled mounting holes.

Steel is typical material for fire-protection cabinets and is required for fire-rated types. Surface-mounted cabinets can be fabricated to match door and trim materials.

Cabinet Material:  Cold-rolled steel sheet.

Retain one of "Semirecessed Cabinet," "Recessed Cabinet," or "Surface-Mounted Cabinet" paragraphs below.

Fully-Recessed Cabinet:

Exposed Flat Trim:  One-piece combination trim and perimeter door frame overlapping surrounding wall surface with exposed trim face and wall return at outer edge (backbend).

Semi-Recessed Cabinet: One-piece combination trim and perimeter door frame overlapping surrounding wall surface with exposed trim face and wall return at outer edge (backbend).

Rolled-Edge Trim: 2-1/2-inch backbend depth

Coordinate cabinet trim material in "Cabinet Trim Material" Paragraph below with door construction. These materials are available for both nonrated and fire-rated cabinets. Delete below if no trim.

Cabinet Trim Material:  Steel sheet.

Door Material:  Steel sheet.

Door Style:  Fully glazed panel with frame.

Door Glazing:  Tempered float glass (clear).

Door Hardware:  Manufacturer's standard door-operating hardware of proper type for cabinet type, trim style, and door material and style indicated.

Provide projecting door pull and friction latch operable with 5 lbs. maximum force.

Provide continuous hinge of same material and finish as trim, permitting door to open 180 degrees.

Finish: Satin stainless steel

Accessories:

Retain "Mounting Bracket" Subparagraph below if required for types of fire-protection cabinets and extinguishers specified.

Mounting Bracket:  Manufacturer's standard steel, designed to secure fire extinguisher to fire-protection cabinet, of sizes required for types and capacities of fire extinguishers indicated, with plated or baked-enamel finish.

Identification:  Lettering complying with authorities having jurisdiction for letter style, size, spacing, and location. Locate as indicated.

Identify fire extinguisher in fire-protection cabinet with the words "FIRE EXTINGUISHER."

Location:  Applied to cabinet door.

Application Process:  Pressure-sensitive vinyl letters.

Lettering Color:  Red.

Orientation:  Vertical.

Materials:

Cold-Rolled Steel:  ASTM A 1008/A 1008M, Commercial Steel (CS), Type B.

Finish:  Baked enamel or powder coat.

Color:  Gloss white.

Stainless-Steel Sheet: ASTM A/240AType 316, dead soft, fully annealed with smooth, flat surface, Finish; #4 directional – satin

Tempered Float Glass:  ASTM C 1048, Kind FT, Condition A, Type I, Quality q3, 3-mm-thick, Class 1 (clear).

FABRICATION

Fire-Protection Cabinets:  Provide manufacturer's standard box (tub) with trim, frame, door, and hardware to suit cabinet type, trim style, and door style indicated.

Weld joints and grind smooth.

Provide factory-drilled mounting holes.

Cabinet Doors:  Fabricate doors according to manufacturer's standards, from materials indicated and coordinated with cabinet types and trim styles.

Fabricate door frames with tubular stiles and rails and hollow-metal design, minimum 1/2-inch-thick.

Cabinet Trim:  Fabricate cabinet trim in one piece with corners mitered, welded, and ground smooth.

GENERAL FINISH REQUIREMENTS

Comply with NAAMM's AMP 500, "Metal Finishes Manual for Architectural and Metal Products," for recommendations for applying and designating finishes.

Protect mechanical finishes on exposed surfaces of fire-protection cabinets from damage by applying a strippable, temporary protective covering before shipping.

Finish fire-protection cabinets after assembly.

Appearance of Finished Work: Noticeable variations in same piece are not acceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

EXECUTION

EXAMINATION

Examine roughing-in for cabinets to verify actual locations before cabinet installation.

Examine walls and partitions for suitable framing depth and blocking where fully recessed or semi-recessed cabinets will be installed.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Retain this article if Project includes recessed or semirecessed cabinets.

Prepare recesses for recessed or semi-recessed fire-protection cabinets as required by type and size of cabinet and trim style.

INSTALLATION

General:  Install fire-protection cabinets in locations and at mounting heights indicated or, if not indicated, at heights indicated below:

Mount Fire Protection Cabinets to provide a handle height for both the Fire-Protection Cabinet and Fire Extinguisher at a maximum 48” above finished floor.  The bottom of surface-mounted Fire Extinguisher Cabinets shall not exceed 27” above finished floor.

Fire-Protection Cabinets: Fasten cabinets to structure, square and plumb.

Retain first subparagraph below if default requirement suits Project.

Unless otherwise indicated, provide semi-recessed fire-protection cabinets. If wall thickness is inadequate for semi-recessed cabinets, provide surface-mounted fire-protection cabinets.

Fasten mounting brackets to inside surface of fire-protection cabinets, square and plumb.

Identification: Apply vinyl lettering at locations indicated.

ADJUSTING AND CLEANING

Remove temporary protective coverings and strippable films, if any, as fire-protection cabinets are installed unless otherwise indicated in manufacturer's written installation instructions.

Adjust fire-protection cabinet doors to operate easily without binding.

On completion of fire-protection cabinet installation, clean interior and exterior surfaces as recommended by manufacturer.

Touch up marred finishes, or replace fire-protection cabinets that cannot be restored to factory-finished appearance. Use only materials and procedures recommended or furnished by fire-protection cabinet and mounting bracket manufacturers.

Replace fire-protection cabinets that have been damaged or have deteriorated beyond successful repair by finish touchup or similar minor repair procedures.

END OF SECTION 10 44 13

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021