MasterSpec 2014

SECTION 10 44 16

FIRE EXTINGUISHERS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes portable, hand-carried fire extinguishers and mounting brackets for fire extinguishers.

Related Requirements:

Section 10 44 13 "Fire Protection Cabinets."

PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

Preinstallation Conference: Conduct conference at Project site.

Retain subparagraph below if additional requirements are necessary; include information about conference.

Review methods and procedures related to fire extinguishers, including:

Schedules and coordination requirements.

ACTION SUBMITTALS

Product Data: For each type of product. Include rating and classification, material descriptions, dimensions of individual components and profiles, and finishes for fire extinguisher and mounting brackets.

Product Schedule: For fire extinguishers. Coordinate final fire-extinguisher schedule with fire-protection cabinet schedule to ensure proper fit and function. Use same designations indicated on Drawings.

INFORMATIONAL SUBMITTALS

Warranty: Sample of special warranty.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For fire extinguishers to include in maintenance manuals.

COORDINATION

Consider retaining this article if fire-protection cabinets are specified by series only or for complex projects.

Coordinate type and capacity of fire extinguishers with fire-protection cabinets to ensure fit and function.

WARRANTY

Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace fire extinguishers that fail in materials or workmanship within specified warranty period.

Failures include:

Hydrostatic test in first subparagraph below is required every five years for water, AFFF, FFFP, dry-chemical-in-stainless-steel-shell, carbon dioxide, and wet-chemical fire extinguishers; test is required every 12 years for other dry-chemical, dry-powder fire extinguishers.

Failure of hydrostatic test according to NFPA 10.

Faulty operation of valves or release levers.

Warranty Period: Five years from date of Substantial Completion.

PRODUCTS

For an explanation of options and Contractor's product selection procedures, see Section 01 60 00 "Product Requirements."

PERFORMANCE REQUIREMENTS

NFPA Compliance: Fabricate and label fire extinguishers to comply with NFPA 10, "Portable Fire Extinguishers."

Fire Extinguishers: Listed and labeled for type, rating, and classification by an independent testing agency acceptable to authorities having jurisdiction.

PORTABLE, HAND-CARRIED FIRE EXTINGUISHERS

Fire Extinguishers: Type, size, and capacity for each fire-protection cabinet and mounting bracket indicated on Drawings.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Amerex Corporation.

Ansul Incorporated; Tyco International.

Potter Roemer LLC.

Or Equal.

Retain "Valves," "Handles and Levers," and "Instruction Labels" subparagraphs below if required.

Valves: Manufacturer's standard.

Handles and Levers: Manufacturer's standard.

Instruction Labels: Include pictorial marking system complying with NFPA 10, Appendix B.

In remaining paragraphs, the letter A, B, C, D, or K indicates the class of fire on which an extinguisher is effective. Class A and Class B are preceded by a rating numeral indicating the extinguisher's relative extinguishing effectiveness. Extinguishers for Class C, Class D, and Class K fires are not required to have a rating numeral.

In retained paragraphs below, insert drawing designation. Use these designations on Drawings to identify each product.

Multipurpose Dry-Chemical Type in Steel Container: UL-rated, with monoammonium phosphate-based dry chemical in enameled-steel container. Provide the following sizes, as indicated and located on Drawings:

2-A:10-B:C, 5-lb.

4A:80B:C.

Retain below for multipurpose dry-chemical-type extinguishers.

Extinguishers shall be fully charged no longer than 4 months from the date of substantial completion.

Insert other types and capacities to suit Project.

MOUNTING BRACKETS

Retain this article if mounting brackets separate from fire-protection cabinets are required.  Delete this article if Mounting Brackets are specified in Section 10 44 13 “Fire Protection Cabinets”

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

Mounting Brackets: Manufacturer's standard steel, designed to secure fire extinguisher to wall or structure, of sizes required for types and capacities of fire extinguishers indicated, with plated or red baked-enamel finish.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Amerex Corporation.

Ansul Incorporated; Tyco International.

Potter Roemer LLC.

Or Equal.

Identification: Lettering complying with authorities having jurisdiction for letter style, size, spacing, and location. Locate as indicated by Architect.

Identify bracket-mounted fire extinguishers with the words "FIRE EXTINGUISHER" in red letter decals applied to mounting surface.

Orientation: Vertical.

EXECUTION

EXAMINATION

Examine fire extinguishers for proper charging and tagging.

Remove and replace damaged, defective, or undercharged fire extinguishers.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

General: Install fire extinguishers in locations indicated and in compliance with requirements of authorities having jurisdiction.

Mount Fire Extinguishers to provide handle height at a maximum of 48” above finish floor, and the bottom of the fire extinguisher is at a maximum of 27” above finish floor.

Mounting Brackets: Fasten mounting brackets to surfaces, square and plumb, at locations indicated.

END OF SECTION 10 44 16

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021