MasterSpec 2014

SECTION 26 05 19

LOW-VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Building wires and cables rated 600 V and less.

Photovoltaic cable, Type PV, rated 2000 V or less.

Connectors, splices, and terminations rated 600 V and less.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Series 27 15 00 "Communications Horizontal Cabling" for cabling used for voice and data circuits.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

ACTION SUBMITTALS

Product Data: For each type of product.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in "Quality Assurance" Article.

Qualification Data: For testing agency.

Field quality-control reports.

QUALITY ASSURANCE

Qualification requirements in the "Testing Agency Qualifications" paragraphs below are in addition to those specified in Section 01 40 02 "Quality Requirements, Contractor Laboratory."

Testing Agency Qualifications: An independent  company, with the experience and capability to  conduct the testing indicated, that is a member company of the  National Electrical Testing Association (NETA) or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

Testing Agency's Field Supervisor: Person currently certified by the National Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

PRODUCTS

CONDUCTORS AND CABLES

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Cerro Wire LLC.

General Cable; General Cable Corporation.

Southwire Company.

Or Equal.

Copper Conductors: Copper, complying with ASTM B 3 for bare annealed copper and with ASTM B 8 for stranded conductors.

Conductor Insulation:

Type THHN and Type THWN-2: Comply with UL 83.

Type XHHW-2: Comply with UL 44.

CONNECTORS AND SPLICES

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

3M.

Ideal Industries, Inc.

O-Z/Gedney; a brand of Emerson Industrial Automation.

Or Equal.

Description: Factory-fabricated connectors and splices of size, ampacity rating, material, type, and class for application and service indicated.

EXECUTION

CONDUCTOR MATERIAL APPLICATIONS

Feeders: Copper.  Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.

Branch Circuits: Copper. Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.

VFC Output Circuit Cables:  Extra-Flexible stranded for all sizes.

PV Circuits:  Copper Solid for No. 10 AWG and smaller, stranded for No. 8 AWG and larger.

CONDUCTOR INSULATION AND WIRING METHODS

This article provides examples of application requirements for conductors and cables. Revise to retain wiring methods for various environments in Project. Add other methods if required. Revise conductor insulation and cable type designations to suit Project conditions, authorities having jurisdiction, and practice. See CEC and UL's "Electrical Construction Equipment Directory" for additional application information about conductor sizes, insulation temperature ratings in cables, and product-use classifications and restrictions.

Service Entrance:  Type XHHW-2, single conductors in raceway.

Exposed Feeders:  Type XHHW-2, single conductors in raceway.

Feeders Concealed in Ceilings, Walls, Partitions, and Crawlspaces: Type XHHW-2, single conductors in raceway.

Coordinate "Feeders Concealed in Concrete, below Slabs-on-Grade, and Underground" Paragraph below with Section 26 05 43 "Underground Ducts and Raceways for Electrical Systems."

Feeders Concealed in Concrete, below Slabs-on-Grade, and Underground:  Type XHHW-2, single conductors in raceway.

Feeders Installed below Raised Flooring: Type XHHW-2, single conductors in raceway.

Exposed Branch Circuits, Including in Crawlspaces: Type THHN/THWN-2, single conductors in raceway.

Branch Circuits Concealed in Ceilings, Walls, and Partitions: Type THHN/THWN-2, single conductors in raceway.

Coordinate "Branch Circuits Concealed in Concrete, below Slabs-on-Grade, and Underground" Paragraph below with Section 26 05 43 "Underground Ducts and Raceways for Electrical Systems."

Branch Circuits Concealed in Concrete, below Slabs-on-Grade, and Underground:  Type XHHW-2, single conductors in raceway.

Branch Circuits Installed below Raised Flooring: Type THHN/THWN-2, single conductors in raceway.

Cord Drops and Portable Appliance Connections: Type SO, hard service cord with stainless-steel, wire-mesh, strain relief device at terminations to suit application.

INSTALLATION OF CONDUCTORS AND CABLES

Conceal cables in finished walls, ceilings, and floors unless otherwise indicated.

Complete raceway installation between conductor and cable termination points according to Section 26 05 33 "Raceways and Boxes for Electrical Systems" prior to pulling conductors and cables.

Use manufacturer-approved pulling compound or lubricant where necessary; compound used must not deteriorate conductor or insulation. Do not exceed manufacturer's recommended maximum pulling tensions and sidewall pressure values.

Use pulling means, including fish tape, cable, rope, and basket-weave wire/cable grips, which will not damage cables or raceway.

Install exposed cables parallel and perpendicular to surfaces of exposed structural members, and follow surface contours where possible.

Support cables according to Section 26 05 29 "Hangers and Supports for Electrical Systems."

CONNECTIONS

Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. If manufacturer's torque values are not indicated, use those specified in UL 486A-486B.

Make splices, terminations, and taps that are compatible with conductor material.

Wiring at Outlets: Install conductor at each outlet, with at least 6 inches of slack.

IDENTIFICATION

Identify and color-code conductors and cables according to Section 26 05 53 "Identification for Electrical Systems."

Identify each spare conductor at each end with identity number and location of other end of conductor, and identify as spare conductor.

SLEEVE AND SLEEVE-SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 26 05 44 "Sleeves and Sleeve Seals for Electrical Raceways and Cabling."

FIRESTOPPING

Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly according to Section 07 84 13 "Penetration Firestopping."

FIELD QUALITY CONTROL

Testing Agency: Engage a qualified testing agency to perform the following tests and inspections.

After installing conductors and cables and before electrical circuitry has been energized, test service entrance and feeder conductors and conductors feeding critical equipment and services for compliance with requirements.

Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

Inspect exposed sections of conductor and cable for physical damage and correct connection according to the single-line diagram.

Test bolted connections for high resistance using one of the following:

A low-resistance ohmmeter.

Calibrated torque wrench.

Thermographic survey.

Inspect compression applied connectors for correct cable match and indentation.

Inspect for correct identification.

Inspect cable jacket and condition.

Insulation-resistance test on each conductor with respect to ground and adjacent conductors. Apply a potential of 1000-V dc for 600-V rated cable for a one-minute duration.

Continuity test on each conductor and cable.

Uniform resistance of parallel conductors.

Consider the cost and benefit of infrared scanning of cables and conductor splices before retaining Initial infrared scanning paragraph.

Initial Infrared Scanning: After Substantial Completion, but before Final Completion, perform an infrared scan of each splice in conductors No. 3 AWG and larger. Remove box and equipment covers so splices are accessible to portable scanner. Correct deficiencies determined during the scan.

Instrument: Use an infrared scanning device designed to measure the temperature or to detect significant deviations from normal values. Provide calibration record for device.

Record of Infrared Scanning: Prepare a certified report that identifies switches checked and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

See Section 01 40 02 "Quality Requirements, Contractor Laboratory" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

Cables will be considered defective if they do not pass tests and inspections.

Test and Inspection Reports: Prepare a written report to record the following:

Procedures used.

Results that comply with requirements.

Results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

END OF SECTION 26 05 19

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: February 14, 2022 Bulletin