MasterSpec 12/15

SECTION 26 05 33

RACEWAYS AND BOXES FOR ELECTRICAL SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Metal conduits, tubing, and fittings.

Nonmetal conduits, tubing, and fittings.

Metal wireways and auxiliary gutters.

Nonmetal wireways and auxiliary gutters.

Surface raceways.

Boxes, enclosures, and cabinets.

Handholes and boxes for exterior underground cabling.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Retain first subparagraph below for underground conduits, handholes, and boxes; delete if incidental exterior underground raceways, handholes, and boxes are specified in this Section.

Section 26 05 43 "Underground Ducts and Raceways for Electrical Systems" for exterior ductbanks, manholes, and underground utility construction.

Section 27 05 28 "Pathways for Communications Systems" for conduits, wireways, surface pathways, innerduct, boxes, faceplate adapters, enclosures, cabinets, and handholes serving communications systems.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

EMT:  Electrical metallic tubing.

FMC:  Flexible metal conduit.

GRC:  Galvanized rigid steel conduit.

LFMC:  Liquid-tight flexible metal conduit.

RNC:  Rigid non-metallic conduit.

ACTION SUBMITTALS

Product Data: For surface raceways, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.

Retain "Shop Drawings" Paragraph below for custom enclosures only.

Shop Drawings: For custom enclosures and cabinets. Include plans, elevations, sections, and attachment details.

INFORMATIONAL SUBMITTALS

Seismic Qualification Certificates: For enclosures, cabinets, and conduit racks and their mounting provisions, including those for internal components, from manufacturer.

PRODUCTS

METAL CONDUITS, TUBING, AND FITTINGS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Allied Tube & Conduit; a part of Atkore International.

Western Tube and Conduit Corporation.

Wheatland Tube Company.

Or Equal.

Listing and Labeling: Metal conduits, tubing, and fittings shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

GRC:  Comply with ANSI C80.1 and UL 6.

PVC-Coated Steel Conduit:  PVC-coated rigid steel conduit.

Comply with NEMA RN 1.

Coating Thickness: 0.040 inch, minimum.

EMT: Comply with ANSI C80.3 and UL 797.

FMC: Comply with UL 1; zinc-coated steel.

LFMC: Flexible steel conduit with PVC jacket and complying with UL 360.

Fittings for Metal Conduit: Comply with NEMA FB 1 and UL 514B.

Coordinate "Conduit Fittings for Hazardous (Classified) Locations" Subparagraph below with Drawings.

Conduit Fittings for Hazardous (Classified) Locations: Comply with UL 886 and CEC.

Fittings for EMT:

Material:  Die cast or steel.

Type:  Compression.

Expansion Fittings: PVC or steel to match conduit type, complying with UL 651, rated for environmental conditions where installed, and including flexible external bonding jumper.

Coating for Fittings for PVC-Coated Conduit: Minimum thickness of 0.040 inch, with overlapping sleeves protecting threaded joints.

NONMETALLIC CONDUITS, TUBING, AND FITTINGS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

CANTEX INC.

Carlon; ABB Group.

Kraloy.

Or Equal.

Listing and Labeling:  Nonmetallic conduits, tubing, and fittings shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

RNC:  Type EPC-40-PVC, complying with NEMA TC 2 and UL 651 unless otherwise indicated.

LFNC: Comply with UL 1660.

Fittings for RNC: Comply with NEMA TC 3; match to conduit or tubing type and material.

Fittings for LFNC: Comply with UL 514B.

Solvent cements and adhesive shall comply with the testing and product requirements of San Diego Air Pollution Control District Rule 67.0 "Architectural Coatings" and Rule 67.21 “Adhesive Material Application Operations.”

METAL WIREWAYS AND AUXILIARY GUTTERS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

B-line, an Eaton business.

Hoffman; a brand of Pentair Equipment Protection.

Square D.

Or Equal.

Description: Sheet metal, complying with UL 870 and NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 12]  unless otherwise indicated, and sized according to CEC.

Metal wireways installed outdoors shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Fittings and Accessories: Include covers, couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for complete system.

Retain one or more options in "Wireway Covers" Paragraph below. If retaining more than one type, indicate locations of each type on Drawings.

Wireway Covers: [Hinged type] [Screw-cover type] [Flanged-and-gasketed type] unless otherwise indicated.

Finish: Manufacturer's standard enamel finish.

NONMETALLIC WIREWAYS AND AUXILIARY GUTTERS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Allied Moulded Products, Inc.

Hoffman; a brand of Pentair Equipment Protection.

Lamson & Sessions.

Or Equal.

Listing and Labeling: Nonmetallic wireways and auxiliary gutters shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Retain one of two "Description" paragraphs below.

Description: Fiberglass polyester, extruded and fabricated to required size and shape, without holes or knockouts. Cover shall be gasketed with oil-resistant gasket material and fastened with captive screws treated for corrosion resistance. Connections shall be flanged and have stainless-steel screws and oil-resistant gaskets.

Description: PVC, extruded and fabricated to required size and shape, and having snap-on cover, mechanically coupled connections, and plastic fasteners.

Fittings and Accessories: Couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings shall match and mate with wireways as required for complete system.

Solvent cements and adhesive primers shall comply with the testing and product requirements of San Diego Air Pollution Control District Rule 67.0 "Architectural Coatings" and Rule 67.21 “Adhesive Material Application Operations.”

SURFACE RACEWAYS

Insert requirements for finish-coat paint color, if applicable, in "Surface Metal Raceways" Paragraph below. See painting Sections for optional field-finish coats.

Listing and Labeling: Surface raceways and tele-power poles shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Surface Metal Raceways: Galvanized steel with snap-on covers complying with UL 5. [Manufacturer's standard enamel finish in color selected by Architect] [Prime coated, ready for field painting].

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Panduit Corp.

Wiremold / Legrand.

Or Equal.

Surface Nonmetallic Raceways: Two- or three-piece construction, complying with UL 5A, and manufactured of rigid PVC with texture and color selected by Architect from [manufacturer's standard] [custom] colors. Product shall comply with UL 94 V-0 requirements for self-extinguishing characteristics.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated.

Panduit Corp.

Wiremold / Legrand.

Or Equal.

Material: [Galvanized steel with ivory baked-enamel finish] [Aluminum with clear anodized finish].

Fittings and Accessories: Dividers, end caps, covers, cutouts, wiring harnesses, devices, mounting materials, and other fittings shall match and mate with tele-power pole as required for complete system.

BOXES, ENCLOSURES, AND CABINETS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hoffman; a brand of Pentair Equipment Protection.

Hubbell Incorporated.

RACO; Hubbell.

Or Equal.

General Requirements for Boxes, Enclosures, and Cabinets:  Boxes, enclosures, and cabinets installed in wet locations shall be listed for use in wet locations.

Sheet Metal Outlet and Device Boxes:  Comply with NEMA OS 1 and UL 514A.

Cast-Metal Outlet and Device Boxes:  Comply with NEMA FB 1, ferrous alloy, Type FD, with gasketed cover.

Metal Floor Boxes:

Material: [Cast metal] [or] [sheet metal].

Type: [Fully adjustable] [Semi-adjustable].

Shape: Rectangular.

Listing and Labeling: Metal floor boxes shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Luminaire Outlet Boxes: Nonadjustable, designed for attachment of luminaire weighing 50 lb. Outlet boxes designed for attachment of luminaires weighing more than 50 lb shall be listed and marked for the maximum allowable weight.

Paddle Fan Outlet Boxes: Nonadjustable, designed for attachment of paddle fan weighing 70 lb.

Listing and Labeling: Paddle fan outlet boxes shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Small Sheet Metal Pull and Junction Boxes: NEMA OS 1.

Cast-Metal Access, Pull, and Junction Boxes: Comply with NEMA FB 1 and UL 1773, galvanized, cast iron with gasketed cover.

Box extensions used to accommodate new building finishes shall be of same material as recessed box.

Device Box Dimensions: [4 inches square by 2-1/8 inches deep] [4 inches by 2-1/8 inches by 2-1/8 inches deep]

Gangable boxes are allowed.

Coordinate "Hinged-Cover Enclosures" Paragraph below with Drawings if hinged-cover enclosures other than NEMA 250, Type 1 are required, such as for very dusty areas; or if consideration should be given to use of NEMA 250, Type 3R or Type 12 enclosures.

Hinged-Cover Enclosures: Comply with UL 50 and NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 12] <Insert type> with continuous-hinge cover with flush latch unless otherwise indicated.

Metal Enclosures: Steel, finished inside and out with manufacturer's standard enamel.

Interior Panels: Steel; all sides finished with manufacturer's standard enamel.

Cabinets:

NEMA 250, [Type 1] [Type 3R] [Type 12]  galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

Hinged door in front cover with flush latch and concealed hinge.

Key latch to match panelboards.

Metal barriers to separate wiring of different systems and voltage.

Accessory feet where required for freestanding equipment.

HANDHOLES AND BOXES FOR EXTERIOR UNDERGROUND WIRING

Verify with manufacturers that units of types specified are available in sizes required. Indicate the size of each enclosure on Drawings, and use a symbol or other notation to differentiate between handholes and pull boxes.

General Requirements for Handholes and Boxes:

Boxes and handholes for use in underground systems shall be designed and identified as defined in CEC, for intended location and application.

Boxes installed in wet areas shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Retain one or more of two paragraphs below to select enclosure type(s) for areas not subject to traffic by vehicles. Indicate location of each type in "Raceway Application" Article. For enclosures with cover options, verify that selected cover is available with load rating specified in "Raceway Application" Article. If retaining more than one type of box and cover combination, indicate location of each type on Drawings.

Polymer-Concrete Handholes and Boxes with Polymer-Concrete Cover: Molded of sand and aggregate, bound together with polymer resin, and reinforced with steel, fiberglass, or a combination of the two.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Armorcast Products Company.

NewBasis.

Oldcastle Precast, Inc.

Or Equal.

Standard: Comply with SCTE 77.

First option in "Configuration" Subparagraph below facilitates bottom conduit entry. Second option may be provided by a separate slab placed in the excavation under an open-bottom enclosure; third option is obtained by molding or fabricating the bottom integrally with the body of unit.

Configuration: Designed for flush burial with [open] [closed] [integral closed] bottom unless otherwise indicated.

Cover: Weatherproof, secured by tamper-resistant locking devices and having structural load rating consistent with enclosure and handhole location.

Cover Finish: Nonskid finish shall have a minimum coefficient of friction of 0.50.

Cover Legend: Molded lettering, ["ELECTRIC."].

Retain "Conduit Entrance Provisions" Subparagraph below if conduit enters enclosure through the side. Otherwise, entry is made through an open bottom or through side openings cut in the field, as specified in "Installation of Underground Handholes and Boxes" Article. Coordinate with Drawings.

Conduit Entrance Provisions: Conduit-terminating fittings shall mate with entering ducts for secure, fixed installation in enclosure wall.

Handholes [12 Inches Wide by 24 Inches Long] and Larger: Have inserts for cable racks and pulling-in irons installed before concrete is poured.

EXECUTION

RACEWAY APPLICATION

Retain this article to specify type of raceway to be installed. Coordinate with conductor and cable wiring methods specified in Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables" and in other electrical, communications, and security Sections.

Outdoors: Apply raceway products as specified below unless otherwise indicated:

Exposed Conduit:  [GRC] [RNC, Type EPC-40-PVC] [RNC, Type EPC-80-PVC].

Concealed Conduit, in masonry or poured-in-place concrete walls, aboveground:  RNC, Type EPC-40-PVC.

Underground Conduit:  RNC, [Type EPC-40-PVC] [Type EPC-80-PVC], [direct buried] [concrete encased].

Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment):  LFMC.

Boxes and Enclosures, Aboveground: NEMA 250, [Type 3R] [Type 4].

Application of Handholes and Boxes for Underground Wiring:

Handholes and Pull Boxes in Driveway, Parking Lot, and Off-Roadway Locations, Subject to Occasional, Non-deliberate Loading by Heavy Vehicles: Polymer concrete SCTE 77, Tier 15 structural load rating.

Handholes and Pull Boxes in Sidewalk and Similar Applications with a Safety Factor for Non-deliberate Loading by Vehicles: Polymer-concrete units, SCTE 77, Tier 8 structural load rating.

Handholes and Pull Boxes Subject to Light-Duty Pedestrian Traffic Only:  Fiberglass-reinforced polyester resin structurally tested according to SCTE 77 with 3000-lbfvertical loading

Indoors: Apply raceway products as specified below unless otherwise indicated:

Exposed, Above 8’-0”, Not Subject to Physical Damage:  EMT.

Exposed, At 8’-0” or Below, Not Subject to Severe Physical Damage:  GRC.

Exposed and Subject to Severe Physical Damage:  GRC.  Raceway locations include the following:

Loading dock.

Corridors used for traffic of mechanized carts, forklifts, and pallet-handling units.

Mechanical rooms.

Gymnasiums.

Concealed in Ceilings and Interior Walls and Partitions:  EMT.

Concealed Conduit, in masonry or poured in place concrete walls:  RNC, Type EPC-40-PVC.

Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment): FMC, except use LFMC in damp or wet locations.

Damp or Wet Locations:  GRC.

Boxes and Enclosures: NEMA 250, Type 1, except use NEMA 250, Type 4 stainless steel in institutional and commercial kitchens and damp or wet locations.

Minimum Raceway Size:  3/4-inch trade size.

Raceway Fittings: Compatible with raceways and suitable for use and location.

Rigid Steel Conduit: Use threaded rigid steel conduit fittings unless otherwise indicated. Comply with NEMA FB 2.10.

PVC Externally Coated, Rigid Steel Conduits: Use only fittings listed for use with this type of conduit. Patch and seal all joints, nicks, and scrapes in PVC coating after installing conduits and fittings. Use sealant recommended by fitting manufacturer and apply in thickness and number of coats recommended by manufacturer.

EMT: Use compression, [steel] [cast-metal for 1-1/2 inch and larger] fittings. Comply with NEMA FB 2.10.

Flexible Conduit: Use only fittings listed for use with flexible conduit. Comply with NEMA FB 2.20.

Coordinate first paragraph below with Drawings.

Install surface raceways only where indicated on Drawings.

Do not install nonmetallic conduit where ambient temperature exceeds 120 deg F.

INSTALLATION

Comply with NECA 1 and NECA 101 for installation requirements except where requirements on Drawings or in this article are stricter. Comply with CEC limitations for types of raceways allowed in specific occupancies and number of floors.

Keep raceways at least 6 inches away from parallel runs of flues and steam or hot-water pipes. Install horizontal raceway runs above water and steam piping.

Complete raceway installation before starting conductor installation.

Comply with requirements in Section 26 05 29 "Hangers and Supports for Electrical Systems" for hangers and supports.

Arrange stub-ups so curved portions of bends are not visible above finished slab.

Install no more than the equivalent of three 90-degree bends in any conduit run except for control wiring conduits, for which fewer bends are allowed. Support within 12 inches of changes in direction.

Conceal conduit and EMT within finished walls, ceilings, and floors unless otherwise indicated. Install conduits parallel or perpendicular to building lines.

Support conduit within 12 inches of enclosures to which attached.

Raceways Embedded in Slabs:

Run conduit larger than 1-inch trade size, parallel or at right angles to main reinforcement. Where at right angles to reinforcement, place conduit close to slab support. Secure raceways to reinforcement at maximum 10-footintervals.

Arrange raceways to cross building expansion joints at right angles with expansion fittings.

Arrange raceways to keep a minimum of [1 inch] [2 inches] <Insert dimension> of concrete cover in all directions.

Do not embed threadless fittings in concrete unless specifically approved by District Construction Manager for each specific location.

Transition from PVC elbows embedded in concrete slabs to exposed ridged conduit shall be with approved fittings and within 3 inches of finished slab or grade.

Stub-ups to Above Recessed Ceilings:

Use EMT or GRC for raceways.

Use a conduit bushing or insulated fitting to terminate stub-ups not terminated in hubs or in an enclosure.

Retain "Threaded Conduit Joints, Exposed to Wet, Damp, Corrosive, or Outdoor Conditions" Paragraph below to require application of protective joint compound to threads of rigid steel conduit and to their fittings where these raceways are installed outdoors or in wet, damp, or corrosive conditions. This optional requirement exceeds CEC rules. If retaining, coordinate with Drawings indicating wet, damp, or corrosive indoor locations.

Threaded Conduit Joints, Exposed to Wet, Damp, Corrosive, or Outdoor Conditions: Apply listed compound to threads of raceway and fittings before making up joints. Follow compound manufacturer's written instructions.

Coat field-cut threads on PVC-coated raceway with a corrosion-preventing conductive compound prior to assembly.

Retain one of first two paragraphs below to exceed CEC requirements. CEC requires insulated bushings or other smooth, rounded entry provisions for conduit terminations at all locations where conductors are No. 4 AWG and larger, regardless of the environment. CEC requires bonding of all service conductors, but does not require bonding to be accomplished with grounding bushings.

Raceway Terminations at Locations Subject to Moisture or Vibration: Use insulating bushings to protect conductors including conductors smaller than No. 4 AWG.

Terminate threaded conduits into threaded hubs or with locknuts on inside and outside of boxes or cabinets. Install bushings on conduits up to 1-1/4-inch trade size and insulated throat metal bushings on 1-1/2-inch trade size and larger conduits terminated with locknuts. Install insulated throat metal grounding bushings on service conduits.

Install raceways square to the enclosure and terminate at enclosures with locknuts. Install locknuts hand tight plus 1/4 turn more.

Do not rely on locknuts to penetrate nonconductive coatings on enclosures. Remove coatings in the locknut area prior to assembling conduit to enclosure to assure a continuous ground path.

Cut conduit perpendicular to the length. For conduits 2-inch trade size and larger, use roll cutter or a guide to make cut straight and perpendicular to the length.

Install pull wires in empty raceways. Use polypropylene or monofilament plastic line with not less than 200-lb tensile strength. Leave at least 12 inches of slack at each end of pull wire. Cap underground raceways designated as spare above grade alongside raceways in use.

Retain "Surface Raceways" Paragraph below if applicable.

Surface Raceways:

Install surface raceway with a minimum 2-inch radius control at bend points.

Secure surface raceway with screws or other anchor-type devices at intervals not exceeding 48 inches and with no less than two supports per straight raceway section. Support surface raceway according to manufacturer's written instructions. Tape and glue are not acceptable support methods.

Install raceway sealing fittings at accessible locations according to CEC and fill them with listed sealing compound. For concealed raceways, install each fitting in a flush steel box with a blank cover plate having a finish similar to that of adjacent plates or surfaces. Install raceway sealing fittings according to CEC.

Install devices to seal raceway interiors at accessible locations. Locate seals so no fittings or boxes are between the seal and the following changes of environments. Seal the interior of all raceways at the following points:

Where conduits pass from warm to cold locations, such as boundaries of refrigerated spaces.

Where an underground service raceway enters a building or structure.

Where otherwise required by CEC.

Comply with manufacturer's written instructions for solvent welding RNC and fittings.

Retain "Expansion-Joint Fittings" Paragraph below unless locations for expansion fittings for RNC are indicated on Drawings.

Expansion-Joint Fittings:

Install in each run of aboveground RNC that is located where environmental temperature change may exceed 30 deg F and that has straight-run length that exceeds 25 feet. Install in each run of aboveground GRC and EMT conduit that is located where environmental temperature change may exceed 100 deg F and that has straight-run length that exceeds 100 feet.

Install type and quantity of fittings that accommodate temperature change listed for each of the following locations:

Revise list below to include all locations in Project with environmental conditions that require considering expansion-joint fittings in conduit runs. For each Project, consider only locations with PVC conduit with straight-run length exceeding 25 feet (7.6 m) or metal conduit in lengths over 100 feet (30 m). Also revise temperature change for each location so it safely represents conditions anticipated. Temperature-change figures below are examples of maximum total swings from the lowest to the highest environmental temperatures at the indicated types of locations and must be revised to represent temperature swings or changes that may occur at Project locations.

Outdoor Locations Not Exposed to Direct Sunlight:  125 deg F temperature change.

Outdoor Locations Exposed to Direct Sunlight:  155 deg F temperature change.

Indoor Spaces Connected with Outdoors without Physical Separation:  125 deg F temperature change.

Attics:  135 deg F temperature change.

Formula in first subparagraph below provides about 15 percent safety factor (extra expansion-contraction capability).

Install fitting(s) that provide expansion and contraction for at least 0.00041 inch per foot of length of straight run per deg F of temperature change for PVC conduits. Install fitting(s) that provide expansion and contraction for at least 0.000078 inch per foot of length of straight run per deg F of temperature change for metal conduits.

Install expansion fittings at all locations where conduits cross building or structure expansion joints.

Install each expansion-joint fitting with position, mounting, and piston setting selected according to manufacturer's written instructions for conditions at specific location at time of installation. Install conduit supports to allow for expansion movement.

Flexible Conduit Connections: Comply with NEMA RV 3. Use a maximum of 72 inches of flexible conduit for recessed and semi-recessed luminaires, equipment subject to vibration, noise transmission, or movement; and for transformers and motors.

Use LFMC in damp or wet locations.

Mount boxes at heights indicated on Drawings. If mounting heights of boxes are not individually indicated, give priority to ADA requirements. Install boxes with height measured to top of box for control devices and to the bottom of box for receptacles and convenience devices, unless otherwise indicated.

Recessed Boxes in Masonry Walls:  Saw-cut opening for box in center of cell of masonry block, and install box flush with surface of wall. Prepare block surfaces to provide a flat surface for a raintight connection between box and cover plate or supported equipment and box.

Horizontally separate boxes mounted on opposite sides of walls so they are not in the same vertical channel.

Locate boxes so that cover or plate will not span different building finishes.

Support boxes of three gangs or more from more than one side by spanning two framing members or mounting on brackets specifically designed for the purpose.

Fasten junction and pull boxes to or support from building structure. Do not support boxes by conduits.

Set metal floor boxes level and flush with finished floor surface.

INSTALLATION OF UNDERGROUND CONDUIT

Retain this article if Project includes small amounts of exterior underground wiring 600 V and less. Delete if Section 26 05 43 "Underground Ducts and Raceways for Electrical Systems" is included in the Project Manual.

Direct-Buried Conduit:

Excavate trench bottom to provide firm and uniform support for conduit. Prepare trench bottom as specified in Section 31 20 00 "Earth Moving" for pipe less than 6 inches in nominal diameter.

Install backfill as specified in Section 31 20 00 "Earth Moving."

After installing conduit, backfill and compact. Start at tie-in point, and work toward end of conduit run, leaving conduit at end of run free to move with expansion and contraction as temperature changes during this process. Firmly hand tamp backfill around conduit to provide maximum supporting strength. After placing controlled backfill to within 12 inches of finished grade, make final conduit connection at end of run and complete backfilling with normal compaction as specified in Section 31 20 00 "Earth Moving."

Install manufactured duct elbows for stub-ups at poles and equipment and at building entrances through floor unless otherwise indicated. Encase elbows for stub-up ducts throughout length of elbow.

Couple steel conduits to ducts with adapters designed for this purpose, and encase coupling with 3 inches of concrete for a minimum of 12 inches on each side of the coupling.

Extend PVC conduit above finish slab or grade a sufficient distance to allow a transition fitting to rigid steel conduit.

Underground Warning Tape: Comply with requirements in Section 26 05 53 "Identification for Electrical Systems."

INSTALLATION OF UNDERGROUND HANDHOLES AND BOXES

Retain this article if Project includes small amounts of exterior underground wiring 600 V and less. Delete if Section 26 05 43 "Underground Ducts and Raceways for Electrical Systems" is included in the Project Manual.

Install handholes and boxes level and plumb and with orientation and depth coordinated with connecting conduits to minimize bends and deflections required for proper entrances.

Unless otherwise indicated, support units on a 6 inch thick level bed of crushed stone or gravel, graded from 1/2-inch sieve to No. 4 sieve and compacted to same density as adjacent undisturbed earth.

Elevation: In paved areas, set so cover surface will be flush with finished grade. Set covers of other enclosures 1 inch above finished grade.

First paragraph below requires Contractor to select hardware to install and support cable. Delete if cable support is not required. If required, revise paragraph to refer Contractor to Drawings, and show specific requirements on Drawings for each enclosure.

Install removable hardware, including pulling eyes, cable stanchions, cable arms, and insulators, as required for installation and support of cables and conductors and as indicated. Select arm lengths to be long enough to provide spare space for future cables but short enough to preserve adequate working clearances in enclosure.

Delete paragraph below if conduits enter enclosure through open bottom.

Field-cut openings for conduits according to enclosure manufacturer's written instructions. Cut wall of enclosure with a tool designed for material to be cut. Size holes for terminating fittings to be used, and seal around penetrations after fittings are installed.

SLEEVE AND SLEEVE-SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 26 05 44 "Sleeves and Sleeve Seals for Electrical Raceways and Cabling."

FIRESTOPPING

Install firestopping at penetrations of fire-rated floor and wall assemblies. Comply with requirements in Section 07 84 13 "Penetration Firestopping."

PROTECTION

Protect coatings, finishes, and cabinets from damage and deterioration.

Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

Repair damage to PVC coatings or paint finishes with matching touchup coating recommended by manufacturer.

END OF SECTION 26 05 33

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021