MasterSpec 03/16

SECTION 26 05 53

IDENTIFICATION FOR ELECTRICAL SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Identification for raceways.

Identification of power and control cables.

Identification for conductors.

Underground-line warning tape.

Warning labels and signs.

Instruction signs.

Equipment identification labels, including arc-flash warning labels.

Miscellaneous identification products.

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for electrical identification products.

Retain "Samples" Paragraph below for single-stage Samples if Project requirements are complex.

Samples: For each type of label and sign to illustrate composition, size, colors, lettering style, mounting provisions, and graphic features of identification products.

Identification Schedule: For each piece of electrical equipment and electrical system components to be an index of nomenclature for electrical equipment and system components used in identification signs and labels. Use same designations indicated on Drawings.

Arc-flash hazard analysis.

PRODUCTS

PERFORMANCE REQUIREMENTS

Comply with ASME A13.1 and IEEE C2

Comply with CEC.

Retain first paragraph below if danger, caution, or safety instruction signs are to be specified.

Comply with 29 CFR 1910.144 and 29 CFR 1910.145.

Comply with ANSI Z535.4 for safety signs and labels.

Comply with [CEC] [and] [Section 26 05 73.19 "Arc-Flash Hazard Analysis"] requirements for arc-flash warning labels.

Retain first paragraph below if retaining self-adhesive products.

Adhesive-attached labeling materials, including label stocks, laminating adhesives, and inks used by label printers, shall comply with UL 969.

Thermal Movements: Allow for thermal movements from ambient and surface temperature changes.

COLOR AND LEGEND REQUIREMENTS

Raceways and Cables Carrying Circuits at 600 V or Less:

Black letters on an orange field.

Legend: Indicate voltage and system or service type.

Color-Coding for Phase- and Voltage-Level Identification, 600 V or Less: Use colors listed below for ungrounded service, feeders, and branch-circuit conductors.

Color shall be factory applied or field applied for sizes larger than No. 8 AWG.

Colors for 208/120-V Circuits:

Phase A: Black.

Phase B: Red.

Phase C: Blue.

Colors for 240-V Circuits:

Phase A: Black.

Phase B: Red.

Colors for 480/277-V Circuits:

Colors specified in first three subparagraphs below are generally used for phase conductors at this voltage.

Phase A: Brown.

Phase B: Orange.

Phase C: Yellow.

Color for Neutral: [White] [or] [gray].

Color for Equipment Grounds: [Bare copper] [Green] [Green with a yellow stripe].

Colors for Isolated Grounds: Green with white stripe.

Raceways and Cables Carrying Circuits at More Than 600 V:

Black letters on an orange field.

Legend: "DANGER - CONCEALED HIGH VOLTAGE WIRING."

Warning Label Colors:

Identify system voltage with black letters on an orange background.

Warning labels and signs include:

Multiple Power Source Warning: "DANGER - ELECTRICAL SHOCK HAZARD - EQUIPMENT HAS MULTIPLE POWER SOURCES."

First subparagraph below applies to OSHA requirements for building operations and does not reflect the clear working space required by CEC.

Workspace Clearance Warning: "WARNING - OSHA REGULATION - AREA IN FRONT OF ELECTRICAL EQUIPMENT MUST BE KEPT CLEAR FOR 36 INCHES."

Retain appropriate articles below to require identification exceeding CEC requirements.  Coordinate retained Section Text articles with "Identification Schedule" Article. Unless specifically noted in retained article title(s), products are suitable for both raceways and conductors.

LABELS

Vinyl Wraparound Labels: Preprinted, flexible labels laminated with a clear, weather- and chemical-resistant coating and matching wraparound clear adhesive tape for securing label ends.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Panduit Corp.

Or Equal.

Snap-around Labels: Slit, pretensioned, flexible, preprinted, color-coded acrylic sleeves, with diameters sized to suit diameters and that stay in place by gripping action.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Marking Services, Inc.

Panduit Corp.

Or Equal.

Self-Adhesive Wraparound Labels: [Preprinted] [Write-on], 3-mil- (0.08-mm-) thick, [polyester] [vinyl] flexible label with acrylic pressure-sensitive adhesive.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Panduit Corp.

Or Equal

Self-Lamination: Clear; UV-, weather- and chemical-resistant; self-laminating, protective shield over the legend. Labels sized to fit the [cable] [raceway] diameter, such that the clear shield overlaps the entire printed legend.

Retain one of two "Marker for Labels" subparagraphs below.

Marker for Labels: Permanent, waterproof, black ink marker recommended by tag manufacturer.

Marker for Labels: Machine-printed, permanent, waterproof, black ink recommended by printer manufacturer.

Retain second subparagraph below for arc-flash warning labels. Coordinate retained subparagraph with Section 26 05 73.19 “Arc-Flash Hazard Analysis" and "Identification Schedule" Article.

Self-Adhesive Labels: Vinyl, thermal, transfer-printed, 3-mil-thick, multicolor, weather- and UV-resistant, pressure-sensitive adhesive labels, configured for display on front cover, door, or other access to equipment unless otherwise indicated.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Panduit Corp.

Or Equal.

Minimum Nominal Size:

1-1/2 by 6 inches for raceway and conductors.

3-1/2 by 5 inches for equipment.

BANDS AND TUBES:

Snap-around, Color-Coding Bands: Slit, pretension, flexible, solid-colored acrylic sleeves, and 2 inches long, with diameters sized to suit diameters and that stay in place by gripping action.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Marking Services, Inc.

Panduit Corp.

Or Equal

Marker Tapes: Vinyl or vinyl-cloth, self-adhesive wraparound type, with circuit identification legend machine printed by thermal transfer or equivalent process.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ideal Industries, Inc.

Marking Services, Inc.

Panduit Corp.

Or Equal

Self-adhesive vinyl tape is generally used to identify flexible conduits and phase conductors. See Part 3 for application instructions.

Self-Adhesive Vinyl Tape: Colored, heavy duty, waterproof, fade resistant; not less than 3 mils thick by 1 to 2 inches wide; compounded for outdoor use.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Marking Services, Inc.

Or Equal

Floor Marking Tape: 2-inch- wide, 5-mil pressure-sensitive vinyl tape, with yellow and black stripes and clear vinyl overlay.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Carlton Industries, LP.

emedco.

Seton Identification Products.

Or Equal

Underground-Line Warning Tape

Common trenching and tape-laying methods are hand, static plow, and vibratory plow. Revise options in "Tape" Subparagraph below if only specific trenching methods are allowed.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Ideal Industries, Inc.

Marking Services, Inc.

Or Equal.

Tape:

Recommended by manufacturer for the method of installation and suitable to identify and locate underground electrical [and communications ] utility lines.

Printing on tape shall be permanent and shall not be damaged by burial operations.

Tape material and ink shall be chemically inert and not subject to degradation when exposed to acids, alkalis, and other destructive substances commonly found in soils.

Color and Printing:

Comply with ANSI Z535.1, ANSI Z535.2, ANSI Z535.3, ANSI Z535.4, and ANSI Z535.5.

Inscriptions for Red-Colored Tapes: "ELECTRIC LINE, HIGH VOLTAGE".

Inscriptions for Orange-Colored Tapes: "TELEPHONE CABLE, CATV CABLE, COMMUNICATIONS CABLE, OPTICAL FIBER CABLE".

Warning Tape Type:

Detectable three-layer laminate, consisting of a printed pigmented polyolefin film, a solid aluminum-foil core, and a clear protective film that allows inspection of the continuity of the conductive core; bright colored,compounded for direct-burial service.

Width: 3 inches.

Overall Thickness: 5 mils.

Foil Core Thickness: 0.35 mil.

Weight: 28 lb/1000 sq. ft..

Tensile according to ASTM D 882: 70 lbf and 4600 psi.

Stenciled Legend: In nonfading, waterproof, [black] <Insert color> ink or paint. Minimum letter height shall be [1 inch] <Insert dimension>.

TAGS

Metal Tags: Brass or aluminum, 2 by 2 by 0.05 inch, with stamped legend, punched for use with self-locking cable tie fastener.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Seton Identification Products.

Or Equal

Retain units in "Nonmetallic Preprinted Tags" Paragraph below for use as phase markers. Specify thicker tags where exposed to damage or rough service.

Nonmetallic Preprinted Tags: Polyethylene tags, [0.015 inch] [0.023 inch] thick, color-coded for phase and voltage level, with factory [screened] [printed] permanent designations; punched for use with self-locking cable tie fastener.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Panduit Corp.

Or Equal

SIGNS

Baked-Enamel Signs:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Carlton Industries, LP.

emedco.

Marking Services, Inc.

Or Equal

Preprinted aluminum signs, punched or drilled for fasteners, with colors, legend, and size required for application.

1/4-inch grommets in corners for mounting.

Nominal Size: 7 by 10 inches.

Metal-Backed Butyrate Signs:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Marking Services, Inc.

Or Equal

Weather-resistant, nonfading, preprinted, cellulose-acetate butyrate signs, with 0.0396-inch galvanized-steel backing and with colors, legend, and size required for application.

1/4-inch grommets in corners for mounting.

Nominal Size: 10 by 14 inches.

Laminated Acrylic or Melamine Plastic Signs:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

emedco.

Marking Services, Inc.

Or Equal

Engraved legend.

Thickness:

For signs up to 20 sq. inches, minimum 1/16-inch-.

For signs larger than 20 sq. inches, 1/8 inch thick.

Retain first option in first subparagraph below for instruction signs; retain second option for identification signs.

Engraved legend with [black letters on white face] [white letters on a dark grey background] <Insert colors>.

[Punched or drilled for mechanical fasteners] [Self-adhesive].

Framed with mitered acrylic molding and arranged for attachment at applicable equipment.

CABLE TIES

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Ideal Industries, Inc.

Marking Services, Inc.

Panduit Corp.

Or Equal

Retain one or more of "General-Purpose Cable Ties," "UV-Stabilized Cable Ties," and "Plenum-Rated Cable Ties" paragraphs below. Coordinate with Part 3 "Installation" Article.

General-Purpose Cable Ties: Fungus inert, self-extinguishing, one piece, self-locking, Type 6/6 nylon.

Minimum Width: 3/16 inch.

Tensile Strength at 73 deg F according to ASTM D 638: 12,000 psi.

Temperature Range: Minus 40 to plus 185 deg F.

Color: Black, except where used for color-coding.

UV-Stabilized Cable Ties: Fungus inert, designed for continuous exposure to exterior sunlight, self-extinguishing, one piece, self-locking, Type 6/6 nylon.

Minimum Width: 3/16 inch.

Tensile Strength at 73 deg F according to ASTM D 638: 12,000 psi.

Temperature Range: Minus 40 to plus 185 deg F.

Color: Black.

Plenum-Rated Cable Ties: Self-extinguishing, UV stabilized, one piece, self-locking.

Minimum Width: 3/16 inch.

Tensile Strength at 73 deg F according to ASTM D 638: 7000 psi.

UL 94 Flame Rating: 94V-0.

Temperature Range: Minus 50 to plus 284 deg F.

Color: Black.

MISCELLANEOUS IDENTIFICATION PRODUCTS

Paint: Comply with requirements in painting Sections for paint materials and application requirements. Retain paint system applicable for surface material and location (exterior or interior).

Fasteners for Labels and Signs: Self-tapping, stainless-steel screws or stainless-steel machine screws with nuts and flat and lock washers.

EXECUTION

PREPARATION

Self-Adhesive Identification Products: Before applying electrical identification products, clean substrates of substances that could impair bond, using materials and methods recommended by manufacturer of identification product.

INSTALLATION

Verify and coordinate identification names, abbreviations, colors, and other features with requirements in other Sections requiring identification applications, Drawings, Shop Drawings, manufacturer's wiring diagrams, and operation and maintenance manual. Use consistent designations throughout Project.

Install identifying devices before installing acoustical ceilings and similar concealment.

Verify identity of each item before installing identification products.

Install identification materials and devices at locations for most convenient viewing without interference with operation and maintenance of equipment. Install access doors or panels to provide view of identifying devices.

Apply identification devices to surfaces that require finish after completing finish work.

Retain one of first two paragraphs below for nonadhesive signs and labels.

Attach signs and plastic labels that are not self-adhesive type with mechanical fasteners appropriate to the location and substrate.

Attach plastic raceway and cable labels that are not self-adhesive type with clear vinyl tape, with adhesive appropriate to the location and substrate.

Cable Ties: For attaching tags. Use general-purpose type, except as listed below:

Outdoors: UV-stabilized nylon.

In Spaces Handling Environmental Air: Plenum rated.

Painted Identification: Comply with requirements in painting Sections for surface preparation and paint application.

Aluminum Wraparound Marker Labels and Metal Tags: Secure tight to surface of conductor or cable at a location with high visibility and accessibility.

Retain "System Identification Color-Coding Bands for Raceways and Cables" Paragraph below if color-coding bands are specified to identify different systems and distinguish one from another.

System Identification Color-Coding Bands for Raceways and Cables: Each color-coding band shall completely encircle cable or conduit. Place adjacent bands of two-color markings in contact, side by side. Locate bands at changes in direction, at penetrations of walls and floors, at 50-foot maximum intervals in straight runs, and at 25-foot maximum intervals in congested areas.

During backfilling of trenches, install continuous underground-line warning tape directly above cable or raceway at 6 to 8 inches below finished grade. Use multiple tapes where width of multiple lines installed in a common trench [or concrete envelope ] exceeds 16 inches overall.

IDENTIFICATION SCHEDULE

Install identification materials and devices at locations for most convenient viewing without interference with operation and maintenance of equipment. Install access doors or panels to provide view of identifying devices.

Identify conductors, cables, and terminals in enclosures and at junctions, terminals, pull points, and locations of high visibility. Identify by system and circuit designation.

Concealed Raceways, Duct Banks, More Than 600 V, within Buildings: Tape and stencil. Stencil legend "DANGER - CONCEALED HIGH-VOLTAGE WIRING" with 3-inch- (75-mm-) high, black letters on 20-inch (500-mm) centers.

Retain "Accessible Raceways, More Than 600 V" Paragraph below for circuits operating at more than 600 V; paragraph contains requirements exceeding those in CEC.

Accessible Raceways, More Than 600 V:  Self-adhesive labels.

Locate identification at changes in direction, at penetrations of walls and floors, at 20-foot maximum intervals in straight runs, and at 15-foot maximum intervals in congested areas.

Retain one of first two paragraphs below, or both. Delete both for existing systems and replace with the existing identification scheme. Paragraphs contain requirements exceeding those in CEC.

Accessible Raceways, 600 V or Less, for Service, Feeder, and Branch Circuits: Identify with self-adhesive vinyl tape applied in bands.

Locate identification at changes in direction, at penetrations of walls and floors, at 20-foot maximum intervals in straight runs, and at 15-foot maximum intervals in congested areas.

Accessible Raceways and Cables within Buildings: Identify the covers of each junction and pull box of the following systems with self-adhesive vinyl labels containing the wiring system legend and system voltage. System legends shall be as follows:

Label Colors:

- System Type			Identification		Background			Lettering

- Lighting and Power	Standard			Orange				White

- Voltage

- Cable Television		CATV			Brown				White

- Clock					CLOCK		Black				White

- Data					DATA			Violet				White

- Emergency Circuits	EMERG		Yellow				Black

- Energy Management	EMS			White				Black

- System

- Fiber Optic System	FIBER			Pink				Black

- Fire Alarm				FIRE			Red				White

- Independent Public	IPA				Gray				White

- Address

- Security/Intrusion		SECUR		Green				White

- Telecommunications	TELECOM		Blue				White

Label Sizes:

- System Type			Size				Background			Lettering

- Lighting and Power	2” (w) x3” (h)		Orange			3/8” White

- Cable TV System		2” (w) x3” (h)		Brown			3/8” White

- Clock System			2” (w) x3” (h)		Black			3/8” White

- Data System			2” (w) x3” (h)		Violet			3/8” White

- Emergency Circuits	2” (w) x3” (h)		Yellow			3/8” Black

- Energy Management	2” (w) x3” (h)		White			3/8” Black

- System

- Fiber Optic System	2” (w) x3” (h)		Pink			3/8” Black

- Fire Alarm System	2” (w) x3” (h)		Red				3/8” White

- Independent Public	2” (w) x3” (h)		Gray			3/8” White

- Address System

- Security/Intrusion		2” (w) x3” (h)		Green			3/8” White

- System

- Telecommunication	2” (w) x3” (h)		Blue			3/8” White

- System

Retain "Power-Circuit Conductor Identification, 600 V or Less" Paragraph below if color-coding of power and lighting conductors for phase- or voltage-level identification is required. If retaining, coordinate with Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables" and revise to indicate extent of color-coding required. For existing buildings, indicate whether requirements apply to both old and new wiring or to new wiring only. Below applies only to phase conductors. Color-coding of grounded and grounding conductors shall be conducted according to CEC. Specify that colors for factory-assembled cable, such as MC and AC, match colors listed below.

Power-Circuit Conductor Identification, 600 V or Less: For conductors in vaults, pull and junction boxes, manholes, and handholes, use color-coding conductor tape to identify the phase.

Power-Circuit Conductor Identification, More Than 600 V: For conductors in vaults, pull and junction boxes, manholes, and handholes, use brass tags colored and marked to indicate phase, and a separate tag with the circuit designation.

Install instructional sign, including the color code for grounded and ungrounded conductors using adhesive-film-type labels.

Control-Circuit Conductor Identification: For conductors and cables in pull and junction boxes, manholes, and handholes, use self-adhesive vinyl labels with the conductor or cable designation, origin, and destination.

Control-Circuit Conductor Termination Identification: For identification at terminations, provide heat shrink preprinted tubes with the conductor designation.

Branch Circuit Conductor Identification:  For conductors in pull and junction boxes use heat shrink preprinted tubes with the conductor branch circuit number and panel designation.

Receptacle and Light Switch Cover Plates:  For all receptacles and local light switch plates, occupancy sensors and other lighting control devices, the cover plates shall be engraved or silkscreened with the panel and circuit number identified.

Retain "Conductors To Be Extended in the Future" Paragraph below for future expansion of circuits or if required for circuits for other purposes. Coordinate with Drawings.

Conductors to Be Extended in the Future: Attach marker tape to conductors and list source.

Auxiliary Electrical Systems Conductor Identification: Identify field-installed alarm, control, and signal connections.

Identify conductors, cables, and terminals in enclosures and at junctions, terminals, and pull points. Identify by system and circuit designation.

Locations of Underground Lines: Identify with underground-line warning tape for power, lighting, communication, and control wiring and optical-fiber cable.

Install underground-line warning tape for cables in raceways.

Workspace Indication: Install floor marking tape to show working clearances in the direction of access to live parts. Workspace shall comply with CEC and 29 CFR 1926.403 unless otherwise indicated. Do not install at flush-mounted panelboards and similar equipment in finished spaces.

Warning Labels for Indoor Cabinets, Boxes, and Enclosures for Power and Lighting: [Baked-enamel warning signs] [Metal-backed, butyrate warning signs].

Identify system voltage with black letters on an orange background.

Apply to exterior of door, cover, or other access.

For equipment with multiple power or control sources, apply to door or cover of equipment, including:

Power-transfer switches.

Controls with external control power connections.

<Insert items>.

Arc-flash analysis should be performed by qualified personnel, with labels printed or made for each piece of equipment, and comply with CEC and Section 26 05 73.19 " Arch-Flash Hazard Analysis."

Arc Flash Warning Labeling: Self-adhesive thermal transfer vinyl labels.

Comply with CEC and ANSI Z535.4.

Comply with Section 26 05 73.19 " Arc-Flash Hazard Analysis" requirements for arc-flash warning labels.

Operating Instruction Signs: [Self-adhesive labels] [Baked-enamel warning signs] [Metal-backed, butyrate warning signs] [Laminated acrylic or melamine plastic signs].

Emergency Operating Instruction Signs: [Self-adhesive labels] [Baked-enamel warning signs] [Metal-backed, butyrate warning signs] [Laminated acrylic or melamine plastic signs] with white legend on a red background with minimum 3/8-inch- high letters for emergency instructions at equipment used for [power transfer] [load shedding] .

Coordinate "Equipment Identification Labels" Paragraph below with electrical Sections. Delete items not in Project.

Equipment Identification Labels: On each unit of equipment, install unique designation label that is consistent with wiring diagrams, schedules, and operation and maintenance manual. Apply labels to disconnect switches and protection equipment, central or master units, control panels, control stations, terminal cabinets, and racks of each system. Systems include power, lighting, control, communication, signal, monitoring, and alarm unless equipment is provided with its own identification.

Labeling Instructions:

Indoor Equipment: Engraved, laminated acrylic or melamine plastic label, punched or drilled for mechanical fasteners. Unless otherwise indicated, provide a single line of text with 1/2-inch-high letters on 1-1/2-inch-high label; where two lines of text are required, use labels 2 inches high.

Outdoor Equipment: Engraved, laminated acrylic or melamine label.

Elevated Components: Increase sizes of labels and letters to those appropriate for viewing from the floor.

Unless labels are provided with self-adhesive means of attachment, fasten them with appropriate mechanical fasteners that do not change the NEMA or NRTL rating of the enclosure.

Equipment To Be Labeled:

Identification labeling of some items listed below may be required by individual Sections or by CEC.

Panelboards: Typewritten directory of circuits in the location provided by panelboard manufacturer. Panelboard identification shall be in the form of an engraved, laminated acrylic or melamine label.

Enclosures and electrical cabinets.

Access doors and panels for concealed electrical items.

Switchgear.

Switchboards.

Transformers: Label that includes tag designation shown on Drawings for the transformer, feeder, and panelboards or equipment supplied by the secondary.

Substations.

Emergency system boxes and enclosures.

Motor-control centers.

Enclosed switches.

Enclosed circuit breakers.

Enclosed controllers.

Variable-speed controllers.

Push-button stations.

Power-transfer equipment.

Contactors.

Remote-controlled switches, dimmer modules, and control devices.

Battery-inverter units.

Battery racks.

Power-generating units.

Monitoring and control equipment.

UPS equipment.

Receptacle and switch cover plates

Voice and data cable terminal equipment.

Master clock and program equipment.

Intercommunication and call system master and staff stations.

Television/audio components, racks, and controls.

Fire-alarm control panel and annunciators.

Security and intrusion-detection control stations, control panels, terminal cabinets, and racks.

Terminals, racks, and patch panels for voice and data communication and for signal and control   functions.

END OF SECTION 26 05 53

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021