MasterSpec 06/15

SECTION 26 05 73.19

ARC-FLASH HAZARD ANALYSIS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes a computer-based, arc-flash study to determine the arc-flash hazard distance and the incident energy to which personnel could be exposed during work on or near electrical equipment.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

Existing to Remain: Existing items of construction that are not to be removed and that are not otherwise indicated to be removed, removed and salvaged, or removed and reinstalled.

One-Line Diagram: A diagram which shows, by means of single lines and graphic symbols, the course of an electric circuit or system of circuits and the component devices or parts used therein.

Protective Device: A device that senses when an abnormal current flow exists and then removes the affected portion from the system.

SCCR: Short-circuit current rating.

Service: The conductors and equipment for delivering electric energy from the serving utility to the wiring system of the premises served.

ACTION SUBMITTALS

Product Data: For computer software program to be used for studies.

Coordinate "Study Submittals" Paragraph below with qualification requirements retained in "Quality Assurance" Article.

Study Submittals: Submit the following submittals after the approval of system protective devices submittals. Submittals [shall] [may] be in digital form.

Arc-flash study input data, including completed computer program input data sheets.

Arc-flash study report; signed, dated, and sealed by a qualified professional engineer.

Submit study report for action prior to receiving final approval of the distribution equipment submittals. If formal completion of studies will cause delay in equipment manufacturing, obtain approval from Architect for preliminary submittal of sufficient study data to ensure that the selection of devices and associated characteristics is satisfactory.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements retained in "Quality Assurance" Article.

Qualification Data: For [Arc-Flash Study Software Developer] [Arc-Flash Study Specialist] [Field Adjusting Agency].

Retain "Product Certificates" Paragraph below to require submittal of product certificates from manufacturers.

Product Certificates: For arc-flash hazard analysis software, certifying compliance with IEEE 1584 and NFPA 70E.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:

Maintenance procedures according to requirements in NFPA 70E shall be provided in the equipment manuals.

Operation and Maintenance Procedures: In addition to items specified in Section 01 78 23 "Operation and Maintenance Data," provide maintenance procedures for use by District personnel that comply with requirements in NFPA 70E.

QUALITY ASSURANCE

Studies shall use computer programs that are distributed nationally and are in wide use. Software algorithms shall comply with requirements of standards and guides specified in this Section. Manual calculations are unacceptable.

Arc-Flash Study Software Developer Qualifications: An entity that owns and markets computer software used for studies, having performed successful studies of similar magnitude on electrical distribution systems using similar devices.

The computer program shall be developed under the charge of a licensed professional engineer who holds IEEE Computer Society's Certified Software Development Professional certification.

Arc-Flash Study Specialist Qualifications: Professional engineer in charge of performing the study, analyzing the arc flash, and documenting recommendations, licensed in the state where Project is located. All elements of the study shall be performed under the direct supervision and control of this professional engineer.

Field Adjusting Agency Qualifications: An independent agency, with the experience and capability to adjust overcurrent devices and to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

PRODUCTS

For an explanation of options and Contractor's product selection procedures, see Section 01 60 00 "Product Requirements."

COMPUTER SOFTWARE DEVELOPERS

Software Developers:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ESA Inc.

Operation Technology, Inc.

Power Analytics, Corporation.

Or Equal.

Comply with IEEE 1584 and NFPA 70E.

Analytical features of device coordination study computer software program shall have the capability to calculate "mandatory," "very desirable," and "desirable" features as listed in IEEE 399.

ARC-FLASH STUDY REPORT CONTENT

Executive summary.

Study descriptions, purpose, basis and scope.

One-line diagram, showing the following:

Protective device designations and ampere ratings.

Cable size and lengths.

Transformer kilovolt ampere (kVA) and voltage ratings.

Motor and generator designations and kVA ratings.

Switchgear, switchboard, motor-control center and panelboard designations.

Study Input Data: As described in "Power System Data" Article.

Retain "Short-Circuit Study Output" Paragraph if a coordination study is not required.

Short-Circuit Study Output: As specified in "Short Circuit Study Output" Paragraph in "Short-Circuit Study Report Contents" Article in Section 26 05 73.13 "Short-Circuit Studies."

Retain "Protective Device Coordination Study Report Contents" Paragraph if a coordination study is required.

Protective Device Coordination Study Report Contents: As specified in "Protective Device Coordination Study Report Contents" Article in Section 26 05 73.16 "Coordination Studies."

Arc-Flash Study Output:

Interrupting Duty Report: Three-phase and unbalanced fault calculations, showing the following for each overcurrent device location:

Voltage.

Calculated symmetrical fault-current magnitude and angle.

Fault-point X/R ratio.

No AC Decrement (NACD) ratio.

Equivalent impedance.

Multiplying factors for 2-, 3-, 5-, and 8-cycle circuit breakers rated on a symmetrical basis.

Multiplying factors for 2-, 3-, 5-, and 8-cycle circuit breakers rated on a total basis.

Incident Energy and Flash Protection Boundary Calculations:

Arcing fault magnitude.

Protective device clearing time.

Duration of arc.

Arc-flash boundary.

Working distance.

Incident energy.

Hazard risk category.

Recommendations for arc-flash energy reduction.

Fault study input data, case descriptions, and fault-current calculations including a definition of terms and guide for interpretation of the computer printout.

ARC-FLASH WARNING LABELS

Comply with requirements in Section 26 05 53 "Identification for Electrical Systems" for self-adhesive equipment labels.  Produce a 3.5-by-5-inch self-adhesive equipment label for each work location included in the analysis.

The label shall have an orange header with the wording, "WARNING, ARC-FLASH HAZARD," and shall include the following information taken directly from the arc-flash hazard analysis:

Location designation.

Nominal voltage.

Flash protection boundary.

Hazard risk category.

Incident energy.

Working distance.

Engineering report number, revision number, and issue date.

Labels shall be machine printed, with no field-applied markings.

EXECUTION

EXAMINATION

Examine Project overcurrent protective device submittals. Proceed with arc-flash study only after relevant equipment submittals have been assembled. Overcurrent protective devices that have not been submitted and approved prior to arc-flash study may not be used in study.

ARC-FLASH HAZARD ANALYSIS

Comply with NFPA 70E and its Annex D for hazard analysis study.

Preparatory Studies:

Retain "Short-Circuit Study Output" Subparagraph below if a coordination study is not required.

Short-Circuit Study Output: As specified in "Short-Circuit Study Output" Paragraph in "Short-Circuit Study Report Contents" Article in Section 26 05 73.13 "Short-Circuit Studies."

Retain "Protective Device Coordination Study Report Contents" Paragraph if a coordination study is required.

Protective Device Coordination Study Report Contents: As specified in "Protective Device Coordination Study Report Contents" Article in Section 26 05 73.16 "Coordination Studies."

Calculate maximum and minimum contributions of fault-current size.

The minimum calculation shall assume that the utility contribution is at a minimum and shall assume no motor load.

The maximum calculation shall assume a maximum contribution from the utility and shall assume motors to be operating under full-load conditions.

Calculate the arc-flash protection boundary and incident energy at locations in the electrical distribution system where personnel could perform work on energized parts.

Include medium- and low-voltage equipment locations, except equipment rated 240-V ac or less fed from transformers less than 125 kVA.

Safe working distances shall be specified for calculated fault locations based on the calculated arc-flash boundary, considering incident energy of 1.2 cal/sq.cm.

Incident energy calculations shall consider the accumulation of energy over time when performing arc-flash calculations on buses with multiple sources. Iterative calculations shall take into account the changing current contributions, as the sources are interrupted or decremented with time. Fault contribution from motors and generators shall be decremented as follows:

Fault contribution from induction motors should not be considered beyond three to five cycles.

Fault contribution from synchronous motors and generators should be decayed to match the actual decrement of each as closely as possible (e.g., contributions from permanent magnet generators will typically decay from 10 per unit to three per unit after 10 cycles).

Arc-flash computation shall include both line and load side of a circuit breaker as follows:

When the circuit breaker is in a separate enclosure.

When the line terminals of the circuit breaker are separate from the work location.

Base arc-flash calculations on actual overcurrent protective device clearing time. Cap maximum clearing time at two seconds based on IEEE 1584, Section B.1.2.

The "Power System Data" Article lists data needed to conduct the overcurrent protective device arc-flash study. Delete data already shown in the one-line diagram on Drawings or included in Section 26 05 73.13 "Short-Circuit Studies" or Section 26 05 73.16 "Coordination Studies." Add data that should be considered in the study results.

POWER SYSTEM DATA

Obtain all data necessary for the conduct of the arc-flash hazard analysis.

Verify completeness of data supplied on the one-line diagram on Drawings [ and under "Preparatory Studies" Paragraph in "Arc-Flash Hazard Analysis" Article]. Call discrepancies to the attention of Architect.

For new equipment, use characteristics submitted under the provisions of action submittals and information submittals for this Project.

For existing equipment, whether or not relocated, obtain required electrical distribution system data by field investigation and surveys, conducted by qualified technicians and engineers.

Retain "Electrical Survey Data" Paragraph below if the arc-flash study is being performed independent of electrical design or on existing equipment. Coordinate requirements with Section 26 05 73.13 "Short-Circuit Studies." Coordinate requirements with Section 26 05 73.16 "Coordination Studies" if required.

Electrical Survey Data: Gather and tabulate the following input data to support study. Comply with recommendations in IEEE 1584 and NFPA 70E as to the amount of detail that is required to be acquired in the field. Field data gathering shall be under the direct supervision and control of the engineer in charge of performing the study, and shall be by the engineer or its representative who holds NETA ETT Level III certification or NICET Electrical Power Testing Level III certification.

Product Data for overcurrent protective devices specified in other Sections and involved in overcurrent protective device coordination studies. Use equipment designation tags that are consistent with electrical distribution system diagrams, overcurrent protective device submittals, input and output data, and recommended device settings.

Obtain electrical power utility impedance at the service.

Power sources and ties.

Short-circuit current at each system bus, three phase and line-to-ground.

Full-load current of all loads.

Voltage level at each bus.

For transformers, include kVA, primary and secondary voltages, connection type, impedance, X/R ratio, taps measured in per cent, and phase shift.

For reactors, provide manufacturer and model designation, voltage rating and impedance.

For circuit breakers and fuses, provide manufacturer and model designation. List type of breaker, type of trip and available range of settings, SCCR, current rating, and breaker settings.

Generator short-circuit current contribution data, including short-circuit reactance, rated kVA, rated voltage, and X/R ratio.

For relays, provide manufacturer and model designation, current transformer ratios, potential transformer ratios, and relay settings.

Busway manufacturer and model designation, current rating, impedance, lengths, and conductor material.

Motor horsepower and NEMA MG 1 code letter designation.

Low-voltage cable sizes, lengths, number, conductor material and conduit material (magnetic or nonmagnetic).

Medium-voltage cable sizes, lengths, conductor material, and cable construction and metallic shield performance parameters.

LABELING

Apply one arc-flash label for 600-V ac, 480-V ac, and applicable 208-V ac panelboards and disconnects and for each of the following locations:

Motor-control center.

Low-voltage switchboard.

Switchgear.

Medium-voltage switch.

Control panel.

APPLICATION OF WARNING LABELS

Install the arc-fault warning labels under the direct supervision and control of the Arc-Flash Study Specialist.

DEMONSTRATION

Engage the Arc-Flash Study Specialist to train District's maintenance personnel in the potential arc-flash hazards associated with working on energized equipment and the significance of the arc-flash warning labels.

END OF SECTION 26 05 73.19

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021