MasterSpec 06/15

SECTION 26 08 00

COMMISSIONING OF ELECTRICAL SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Purpose

Commissioning (Cx) of specific electrical systems noted in this section for functionality, process and operation.  Acceptance testing, product testing and equipment testing are specified in each individual Division 26 specification section.

For example, an emergency power system has testing of engine generator, automatic transfer switch and switchboards specified in each individual section.  Commissioning entire emergency power system, consisting of all components, is specified in this section.

Retain systems below that will be commissioned. Coordinate with retained " Pre-Functional Checklists " Paragraph in "Informational Submittals" Article. Only systems are mentioned in "Summary" Article; equipment-specific checklists are listed in " Pre-Functional Checklists " Article.

Section includes Cx process requirements for the following electrical components, systems, assemblies, and equipment:

Electrical equipment connected to Normal power system, including:

Motor-control centers.

Transformers.

[Primary] [and] [secondary] service electrical systems.

[Distribution] [and] [branch-circuit] panelboards.

Lightning protection systems.

Grounding systems.

Electrical equipment connected to Essential power systems that provide an alternative source of power in the absence of power from the Normal power system, including:

Motor-control centers.

[Primary] [and] [secondary] service electrical systems.

[Distribution] [and] [branch-circuit] panelboards.

Lighting protection systems.

Grounding systems.

Generators.

UPS.

Controls and instrumentation, including:

Equipment monitoring systems.

Energy monitoring and control systems.

Electrical metering and metering system.

Demand response systems.

Lighting control systems.

Systems testing and verification, including [Normal] [and] [Essential] power systems[, and transitions from Normal to Essential power systems and back].

Renewable Energy Systems

Photovoltaic system.

HVAC/DDC Lighting BAS interface.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 01 91 13 "General Commissioning Requirements" for general Cx process requirements and Cx team responsibilities.

Section 23 09 23 "Direct Digital Control (DDC) System for HVAC for DDC Cx coordination requirements.

Section 26 31 00 “Photovoltaic System” for photovoltaic system Cx coordination requirements.

REFERENCES

NETA Standards: Currently enforced edition.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

BAS: Building Automation System.

DDC: Direct Digital Control

Essential Power Systems: A power system that a facility transitions to in absence of Normal power.  Includes all systems classified as "standby" or "emergency," including "legally required."

Low Voltage: 600 V and below.

Medium Voltage: 601 V and above.

Normal Power System: A power system that provides primary power to a facility.

"Systems," "Assemblies," "Subsystems," "Equipment," and "Components": Where these terms are used together or separately, they shall mean "as-built" systems, assemblies, subsystems, equipment, and components.

For additional Cx terminology definitions and abbreviations, see Section 01 91 13 "General Commissioning Requirements."

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 01 40 00 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For testing agency and Title 24 Certified Technicians

Pre-Functional Checklists (PFCs), including:

Revise list of PFCs below to suit Project. Coordinate list with appropriate related Sections' content. Below are examples of common PFCs.

Coordinate nomenclature of PFCs with field quality-control provisions in the corresponding sections.

Instrumentation and control for electrical systems.

Instrumentation and control for lighting control systems.

Low-voltage power cables.

Control voltage power cables.

Electrical feeders and branch circuits.

Liquid-filled transformers.

Dry-type transformers.

Instrument transformers.

Switchgear and switchboard assemblies.

Metal-enclosed bus duct.

Busway.

Motor-control centers.

Low-voltage motor starters.

Low-voltage air circuit breakers.

Low-voltage insulated case circuit breakers.

Low-voltage network protectors.

Low-voltage air switches.

Low-voltage surge protective devices.

Delete first seven subparagraphs below if there is no medium-voltage equipment in Project.

Medium-voltage power cables.

Medium-voltage circuit breakers.

Medium-voltage motor starters.

Medium-voltage air circuit breakers.

Medium-voltage vacuum circuit breakers.

Medium-voltage air switches.

Medium-voltage surge protective devices.

Protective relays.

Metering devices.

Molded-case circuit breakers.

Low-voltage power circuit breakers.

Grounding systems.

Ground-fault protection systems.

Panelboards.

Receptacles and devices.

Engine generators.

Automatic transfer switches.

Variable-frequency drives.

AC synchronous motors and generators.

AC induction motors and generators.

DC motors and generators.

Battery systems.

Battery chargers.

Flooded lead-acid batteries.

Flooded lead-calcium batteries.

VRLA batteries.

UPS systems.

Power factor correction equipment, including capacitors, dry-type reactors (both shunt and current-limiting), and liquid-filled reactors (both shunt and current-limiting).

Interior and exterior Lighting and controls

CLOSEOUT SUBMITTALS

Retain this article to require submittal of data for O&M plans developed by CxA.

Operation and Maintenance (O&M) Data: For electrical systems and components to include in O&M manuals.

Title 24 Power Distribution Testing:

Certificate of Compliance for power distribution system.

Copies of signed Certificates of Installation.

Copies of signed acceptance forms.

Completed testing script.

Title 24 Lighting and Controls Testing:

Certificate of Compliance for lighting and lighting control systems.

Copies of signed Certificates of Installation.

Copies of signed acceptance forms.

Completed testing script.

Emergency Lighting/Inverter:

Certificate of Compliance for operation of emergency lighting system and inverter.

Copies of signed Certificates of Installation.

Copies of signed acceptance forms.

Completed testing script.

DDC/HVAC lighting BAS Interface:

Certificate of Compliance for DDC/HVAC lighting interface with BAS.

Completed Cx script.

Emergency Generator and Automatic Transfer Switch:

Certificate of Compliance for engine/generator and automatic transfer switch.

Copies of signed Certificates of Installation.

Copies of signed acceptance forms.

Completed testing script

Photovoltaic System:

Certificate of Compliance for photovoltaic system.

Copies of signed Certificates of Installation.

Copies of signed acceptance forms.

Completed testing script.

QUALITY ASSURANCE

Testing Agency Qualifications:

Member company of NETA; NETA registered and certified.

Regularly engaged in Cx of electrical equipment, devices, installations, and systems, with at least five years of documented experience.

All Cx shall be per NETA standards.

Testing agency’s lead, on-site, technical person shall be currently certified by NETA in electrical power distribution system testing.

Testing agency’s engineers and technicians must be regularly employed by testing agency for Cx testing services.

Title 24 Certified Technician Qualifications:

Certified by California State Energy Commission for performing Title 24 Cx of power and lighting control systems as installed.

Independent third party; not an employee of Contractor.

Testing Equipment and Instrumentation Quality and Calibration: For test equipment and instrumentation required to perform electrical Cx work, perform the following:

Submit test equipment and instrumentation list. For each equipment or instrument, identify:

Equipment/instrument identification number.

Planned Cx application or use.

Manufacturer, make, model, and serial number.

Calibration history, including certificates from agencies that calibrate the equipment and instrumentation.

Test equipment and instrumentation shall meet the following criteria:

Capable of testing and measuring performance within specified acceptance criteria.

Be calibrated at manufacturer's recommended intervals with current calibration tags permanently affixed to instrument being used.

Be maintained in good repair and operating condition throughout duration of use on Project.

Be recalibrated/repaired if dropped or damaged in any way since last calibrated.

Proprietary Test Instrumentation and Tools:

Equipment Manufacturer's Proprietary Instrumentation and Tools: For installed equipment included in Cx process, test instrumentation and tools manufactured or prescribed by equipment manufacturer to service, calibrate, adjust, repair, or otherwise work on its equipment or required as a condition of equipment warranty, perform the following:

Submit proprietary instrumentation and tools list. For each instrument or tool, identify:

Instrument or tool identification number.

Equipment schedule designation of equipment for which instrument or tool is required.

Manufacturer, make, model, and serial number.

Calibration history, including certificates from agencies that calibrate the instrument or tool, where appropriate.

Include a separate list of proprietary test instrumentation and tools in O&M manuals.

PRODUCTS (Not Used)

EXECUTION

PRE-FUNCTIONAL CHECKLISTS (PFCs)

Prepare detailed PFCs for electrical systems, subsystems, equipment, and components.  Complete and submit PFCs.

COMMISSIONING AUTHORITY (CxA) PRE-FUNCTIONAL CHECKLIST (PFC) REVIEW

Review and provide written comments on Contractor’s draft PFCs.

Return draft PFCs review comments within 10 days of receipt.

When review comments have been resolved, CxA will mark Contractor’s final PFCs, "Approved for Use, (date)."

Use only PFCs, marked "Approved for Use, (date)."

GENERAL TESTING REQUIREMENTS

Engage a third party testing agency and a third party Certified Title 24 Technician to perform specified tests and inspection services.

Perform routine insulation resistance, continuity, and phase rotation tests for all distribution and utilization equipment prior to and in addition to specified tests.

Notify District Construction Manager and District Electrical Inspector no fewer than 14 working days prior to commencement of any Cx.

Report any system, material, or workmanship that is found defective on the basis of Cx to District Construction Manager and District Electrical Inspector, along with recommendations for corrective action.

INSPECTION AND TEST PROCEDURES

Provide testing agency a copy of related Contract Documents, including drawings, specifications, engineer-reviewed submittals and other necessary information.

Supply a suitable source of power to each site and location per testing agency requirements.

Notify testing agency when equipment becomes available for Cx and tests. Coordinate work with accepted project schedule.

Testing agency shall review and evaluate all received documents and immediately notify Contractor, District Electrical Inspector and District Construction Manager of any discrepancies in the documents and any other issues or requirements.

Testing agency shall provide and comply with:

Test procedures for each individual specification section prior to any test and after thorough evaluation of the system. Testing shall conform to NETA specifications and standards for electrical power distribution equipment and systems and manufacturer’s instructions.

Refer to each individual specification section for testing requirements.

Inspect installed equipment and report non-compliance with Contract Documents and governing codes prior to Cx and testing.

Certify that electrical systems, subsystems, and equipment have been installed, calibrated, and started, and that they are operating according to Contract Documents and approved Shop Drawings and submittals.

Certify that electrical instrumentation and control systems have been completed and calibrated, that they are operating according to the Contract Documents and approved Shop Drawings and submittals, and that pretest set points have been recorded.

Set systems, subsystems, and equipment into operating mode to be tested according to approved test procedures (for example, normal shutdown, normal auto position, normal manual position, unoccupied cycle, emergency power, alarm conditions).

Measure capacities and effectiveness of systems, assemblies, subsystems, equipment, and components, including operational and control functions to verify compliance with acceptance criteria.

Test systems, assemblies, subsystems, equipment, and components operating modes, interlocks, control responses, and responses to abnormal or emergency conditions, and response according to acceptance criteria.

PFCs: Prepare and submit detailed PFCs for electrical systems, subsystems, equipment, and components.

Contributors to development of PFCs include:

Electrical systems and equipment installers.

Electrical instrumentation and controls installers.

Perform tests using design conditions, whenever possible.

Simulated conditions may, with approval of Architect and District Construction Manager, be imposed using an artificial load when it is impractical to test under design conditions. Before simulating conditions, calibrate testing instruments. Provide equipment to simulate loads. Set simulated conditions as directed by CxA, and document simulated conditions and methods of simulation. After tests, return configurations and settings to normal operating conditions.

Cx test procedures may direct that set points be altered when simulating conditions is impractical.

Cx test procedures may direct that sensor values be altered with a signal generator when design or simulating conditions and altering set points are impractical.

If tests cannot be completed because of a deficiency outside scope of electrical system, document deficiency and report it to District Construction Manager. After deficiencies are resolved, reschedule tests.

If seasonal testing is specified, complete appropriate initial performance tests and documentation and schedule seasonal tests.

Coordinate schedule with, and perform, Cx activities at direction of CxA.

Comply with PFC requirements, including material verification, installation checks, startup, and performance tests requirements specified in Sections specifying electrical systems and equipment.

Provide technicians, instrumentation, tools, and equipment to complete and document the following:

Performance tests.

Demonstration of a sample of performance tests.

Cx tests.

Cx test demonstrations.

TITLE 24 POWER DISTRIBUTION COMMISSIONING (Cx)

Title 24 Testing of Power Distribution System

Provide all material, equipment, labor, and technical supervision to perform such tests and inspections.

Purpose of Tests:  To assure that all tested electrical equipment is operational and within parameters of CCR Title 24, and installed in accordance with Contract Documents.

The following systems shall be certified by Title 24 Certified Technician:

Electrical service metering.

Disaggregation of electrical circuits.

Voltage Drop for feeders and branch circuits.

Circuit controls for 120 volt receptacles.

Title 24 Certified Technician shall provide:

Test Plan.

Functional Performance Testing Documentation and Training.

Test Report.

Installation and Acceptance Compliance Forms.

TITLE 24 LIGHTING CONTROL TESTING

Title 24 Testing of lighting system includes:

          - Automatic Day Lighting Control.

          - Occupant sensor.

          - Automatic Time Switch Control.

          - Demand Responsive Controls.

          - Outdoor Motion Sensor.

          - Outdoor Lighting Shut Off Controls.

Certified Title 24 Technician shall provide:

Test Plan.

Functional Performance Testing.

Documentation and Training.

Test Report.

Installation, Acceptance, and Certificate of Compliance Forms.

DDC/HVAC LIGHTING BAS INTERFACE COMMISSIONING (Cx)

DDC/HVAC interface Cx includes:

Verify that each lighting controller, zone or space is monitored as to on/off status.

Verify that each lighting controller, zone or space can be controlled on or off and status is changed accordingly.

Verify that each occupancy/vacancy switch is controllable on or off.

CxA shall provide:

Cx Plan.

Functional Performance Testing.

Cx Report.

EMERGENCY LIGHTING AND INVERTER TESTING

Emergency lighting and inverter testing includes:

Verify all emergency lighting circuits and fixtures are properly circuited.

Simulate a power outage and verify emergency lighting fixtures are illuminated.

During simulation, inverter shall be left energized for 90 minute run time.  Verify that all emergency lighting fixtures are illuminated during this period.

Provide:

Test Plan.

Functional Performance Testing.

Test Report.

EMERGENCY GENERATOR AND AUTOMATIC TRANSFER SWITCH COMMISSIONING (Cx)

Emergency engine generator and automatic transfer switch testing includes:

Simulate main utility power loss and verify automatic engine/generator starting and transfer of emergency loads to engine/generator.  Verify and record amount of time this function required.

Simulate return of utility power and after programmed delay, verify loads have been retransferred back to utility power.  Verify engine/generator is in cool down mode prior to automatically shutting down

During cool down mode, simulate another main utility power loss and verify emergency loads are automatically re-transferred via automatic transfer switch to engine/generator.

Simulate return of utility power and verify emergency loads are transferred back to utility power.

Verify engine cool down time delay and automatic shut-down of engine/generator.

Provide:

Test Plan.

Functional Performance Testing.

Test Report.

PHOTOVOLTAIC SYSTEM TESTING

        - Testing agency shall perform system function test upon completion of equipment tests as defined in this section and as required by other sections.

        - Purpose of System Function Tests: Verify proper interaction of all sensing, processing, and action devices.

        - Implementation:

          - Develop test parameters for purpose of evaluation performance of all integral components and their functioning as a complete unit within design requirements.

          - Test all interlocking devices.

          - Record operation of alarms and indicating devices.

Cx TESTS FOR ELECTRICAL SYSTEMS

Verification of Normal Power System Operation:

Prerequisites: Acceptance of results for PFCs for Division 26 electrical components associated with Normal power system.

Equipment and Systems to Be Tested: Division 26 electrical equipment.

Test Purpose: Verify operation of Normal power system.

Test Conditions: Energize components of Normal power system, one at a time.

Acceptance Criteria: Proper operation of Normal power system over a [24][48]-hour period.

Verification of Essential Power Systems Operation:

Prerequisites:

Acceptance of results for PFCs for Division 26 electrical components associated with Essential power systems.

Completion of "Verification of Normal Power System Operation" tests.

Equipment and Systems to Be Tested: Division 26 electrical equipment.

Test Purpose: Verify operation of Essential power systems.

Test Conditions:

Energize components of Normal power system.

Simulate a failure of Normal power system.

Acceptance Criteria: Transfer of power from Normal to Essential power systems within project requirements.

Verification of Control and Instrumentation:

Prerequisites: Acceptance of results for PFCs.

Section 26 09 13 "Electrical Power Monitoring and Control."

Section 26 09 23 "Lighting Control Devices."

Section 26 09 43.16 "Addressable-Luminaire Lighting Controls."

Section 26 09 43.23 "Relay-Based Lighting Controls."

Section 26 27 13 "Electricity Metering."

Section 26 35 33 "Power Factor Correction Equipment."

Test Purpose: Verify operation of control and monitoring systems for Normal and Essential power systems.

Test Conditions:

Energize components of Normal power system.

Test operation of equipment.

Acceptance Criteria: Operation of equipment according to project requirements.

      - DEFICIENCIES

Correct all deficiencies reported by testing agency, District Electrical Inspector, and CxA.  Repeat Cx and system function tests as necessary to achieve conformance with requirements, at no additional cost to District.

END OF SECTION 26 08 00

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021