MasterSpec 2014

SECTION 26 09 23

LIGHTING CONTROL DEVICES

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Photoelectric switches.

Demand Response Device

Outdoor motion sensors.

Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 26 08 00 “Commissioning of Electrical Systems.”

Section 26 27 26 "Wiring Devices" for wall-box dimmers, wall-switch occupancy sensors, and manual light switches.

ACTION SUBMITTALS

Product Data: For each type of product.

Shop Drawings: Show installation details for occupancy and light-level sensors.

Retain first subparagraph below unless control connections are indicated on Drawings.

Interconnection diagrams showing field-installed wiring.

Include diagrams for power, signal, and control wiring.

INFORMATIONAL SUBMITTALS

Field quality-control reports.

Coordinate “Qualification Data” paragraph below with qualification requirements in "Quality Assurance"   Article.

Qualification Data: For technician performing lighting system acceptance certification.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For each type of lighting control device to include in emergency, operation, and maintenance manuals.

Acceptance Testing Certification:  For each interior and exterior space as required by CBC Title 24 Part 6.

QUALITY ASSURANCE

Certified Acceptance Technician Qualifications:  Acceptance Technician certified and registered with the State of California as required by CBC Title 24 Part 6.

PRODUCTS

SWITCHES

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Intermatic, Inc.

Leviton Manufacturing Co., Inc.

Tyco Electronics Corporation; a TE Connectivity Ltd. company.

Or Equal.

Retain one of two "Description" paragraphs below. Light-level range is typical for dusk-to-dawn lighting applications. An inductive rating for a switch means it is UL tested at a 50 percent power factor.

First "Description" Paragraph describes a device with built-in, metal-oxide-varistor surge protection, a selection of contact ratings, and a range of adjustments to orient the photocell. These features allow flexibility in making the device suitable for a range of mounting and control situations.

Second "Description" Paragraph describes a device with less-effective surge protection, having a fixed load-breaking contact capacity. Its main application is control of a single lighting fixture. It is designed for mounting on a fixture.

Description: Solid state, with [SPST] [DPST] dry contacts rated for 1800-VA tungsten, to operate connected relay, contactor coils, or microprocessor input; complying with UL 773A and compatible with ballasts and LED amps.

Listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Light-Level Monitoring Range: 1.5 to 10 fc, with an adjustment for turn-on and turn-off levels within that range[, and a directional lens in front of the photocell to prevent fixed light sources from causing turn-off].

Time Delay: Fifteen second minimum, to prevent false operation.

Surge Protection: Metal-oxide varistor.

Mounting: Twist lock complies with IEEE C136.10, with base-and-stem mounting or stem-and-swivel mounting accessories as required to direct sensor to the north sky exposure.

Failure Mode:  Luminaire stays ON.

Description: Solid state, with [SPST] [DPST] dry contacts rated for 1800 VA, to operate connected load, complying with UL 773.

Listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Light-Level Monitoring Range: 1.5 to 10 fc, with an adjustment for turn-on and turn-off levels within that range.

Time Delay: Thirty-second minimum, to prevent false operation.

Lightning Arrester: Air-gap type.

Mounting: Twist lock complying with NEMA C136.10, with base.

Failure Mode:  Luminaire stays ON.

Description Paragraph below describes a low-voltage control device to be used with power pack. It may be used to control one or several luminaires or be connected to a lighting control panelboard, and it is designed for installation on building exterior or roof.

SWITCHBOX-MOUNTED OCCUPANCY SENSORS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Leviton Manufacturing Co., Inc.

Lutron Electronics Co., Inc.

Watt Stopper.

Or Equal.

Each manufacturer's switch rating is different; however, rated design values are generally not less than those stated in "General Requirements for Sensors" Paragraph below.

General Requirements for Sensors: Automatic-wall-switch occupancy sensor, suitable for mounting in a single gang switchbox,[, with provisions for connection to BAS] [using hardwired connection] [using wireless connection].

Listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application, and shall comply with California Title 24.

Occupancy Sensor Operation: Unless otherwise indicated, turn lights on when coverage area is occupied, and turn lights off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 15 minutes.

Operating Ambient Conditions: Dry interior conditions, 32 to 120 deg F.

Switch Rating: Not less than 800-VA [ballast] [or] [LED] at 120 V, 1200-VA [ballast] [or] [LED] at 277 V, and 800-W incandescent.

"WS1" and "WS2" in "Wall-Switch Sensor Tag WS1" and "Wall-Switch Sensor Tag WS2" paragraphs below are a suggested marking system on Drawings when detectors with different sensor characteristics are required.

Wall-Switch Sensor Tag WS1:

Standard Range: 180-degree field of view, field adjustable from 180 to 40 degrees; with a minimum coverage area of [900 sq. ft.] [2100 sq. ft].

Sensing Technology: [PIR] [Dual technology - PIR and ultrasonic].

Switch Type: [SP.] [SP, dual circuit.] [SP, manual "on," automatic "off."] [SP, field selectable automatic "on," or manual "on" automatic "off."]

Capable of controlling load in three-way application.

Voltage: [Match the circuit voltage] [120 V] [277 V] [Dual voltage, 120 and 277 V]; [passive-infrared] [dual-technology] type.

Ambient-Light Override: Concealed, field-adjustable, light-level sensor from 10 to 150 fc. The switch prevents the lights from turning on when the light level is higher than the set point of the sensor.

Retain one of two "off" time-delay subparagraphs below.

Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

Concealed "off" time-delay selector at 30 seconds, and 5, 10, and 20 minutes.

Adaptive Technology: Self-adjusting circuitry detects and memorizes usage patterns of the space and helps eliminate false "off" switching.

"Wall-Switch Sensor Tag WS2" Paragraph below is typical for square and near-square rectangular rooms.

Wall-Switch Sensor Tag WS2:

Standard Range: 210-degree field of view, with a minimum coverage area of 900 sq. ft..

Sensing Technology: PIR.

Switch Type: [SP.] [SP, dual circuit.] [SP, manual "on," automatic "off."] [SP, field selectable automatic "on," or manual "on" automatic "off."]

Capable of controlling load in three-way application.

Voltage: [Match the circuit voltage] [120 V] [277 V] [Dual voltage, 120 and 277 V]; [passive-infrared] [dual-technology] type.

Ambient-Light Override: Concealed, field-adjustable, light-level sensor from 10 to 150 fc. The switch prevents the lights from turning on when the light level is higher than the set point of the sensor.

Retain one of two "off" time-delay subparagraphs below.

Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

Concealed "off" time-delay selector at 30 seconds, and 5, 10, and 20 minutes.

Adaptive Technology: Self-adjusting circuitry detects and memorizes usage patterns of the space and helps eliminate false "off" switching.

Coordinate color of switch and faceplate with Section 262726 "Wiring Devices.”

Color [White] [Black] <Insert color>.

Faceplate: Color matched to switch.

Coordinate outdoor lighting motion sensors with security camera (CCTV) motion sensors.

OUTDOOR MOTION SENSORS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Leviton Manufacturing Co., Inc.

Lithonia Lighting; Acuity Brands Lighting, Inc.

Watt Stopper.

Or Equal.

General Requirements for Sensors: Solid-state outdoor motion sensors.

Retain features in subparagraphs below applicable to motion sensors for Project.

Listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application, and shall comply with California Title 24.

[PIR] [Dual-technology (PIR and infrared)] type, weatherproof. Detect occurrences of 6-inch-minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. Comply with UL 773A.

Switch Rating:

Lighting-Fixture-Mounted Sensor: [1000-W incandescent, 500-VA fluorescent/LED].

Separately Mounted Sensor: Dry contacts rated for 20-A [ballast] [or] [LED] load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac. Sensor has 24-V dc, 150-mA, Class 2 power source, as defined by CEC.

Switch Type: [SP.] [SP, dual circuit.] [SP, manual "on," automatic "off."] [SP, field selectable automatic "on," or manual "on" automatic "off."][ With bypass switch to override the "on" function in case of sensor failure.]

Voltage: [Match the circuit voltage] [120-V] [277-V] type.

Detector Coverage:

Standard Range: 210-degree field of view, with a minimum coverage area of 900 sq. ft.

Long Range: 180-degree field of view and 110-foot detection range.

Ambient-Light Override: Concealed, field-adjustable, light-level sensor from 10 to 150 fc. The switch prevents the lights from turning on when the light level is higher than the set point of the sensor.

Retain one of two "off" time-delay subparagraphs below.

Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

Concealed "off" time-delay selector at 30 seconds, and 5, 10, and 20 minutes.

Adaptive Technology: Self-adjusting circuitry detects and memorizes usage patterns of the space and help eliminate false "off" switching.

Operating Ambient Conditions: Suitable for operation in ambient temperatures ranging from minus 40 to plus 130 deg F, rated as "raintight" according to UL 773A.

DEMAND RESPONSE DEVICE

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Leviton Manufacturing Co., Inc.

Lutron Electronics Co., Inc.

Watt Stopper.

Or equal.

The interior lighting control power pack shall have provisions to accept an input signal for demand response compliance.

The demand response device can either be integral with the power supply or be a stand-alone module.

LIGHTING CONTACTORS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Allen-Bradley/Rockwell Automation.

ASCO Power Technologies, LP; a business of Emerson Network Power.

Eaton Corporation.

Or Equal.

Description: Electrically operated and [mechanically] [electrically] held, combination-type lighting contactors with [fusible switch] [non-fused disconnect], complying with NEMA ICS 2 and UL 508.

Revise subparagraphs below, if required, for specific ratings; or indicate on Drawings. Coordinate control voltage with lighting control system if used.

Current Rating for Switching: Listing or rating consistent with type of load served, including tungsten filament, inductive, and high-inrush ballast (ballast with 15 percent or less total harmonic distortion of normal load current).

Fault Current Withstand Rating: Equal to or exceeding the available fault current at the point of installation.

Enclosure: Comply with NEMA 250.

Provide with control and pilot devices as indicated on Drawings, matching the NEMA type specified for the enclosure.

CONDUCTORS AND CABLES

Power Wiring to Supply Side of Remote-Control Power Sources: Not smaller than No. 12 AWG. Comply with requirements in Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

Classes 2 and 3 Control Cable: Multiconductor cable with stranded-copper conductors not smaller than No. 18 AWG. Comply with requirements in Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

Class 1 Control Cable: Multiconductor cable with stranded-copper conductors not smaller than No. 14 AWG. Comply with requirements in Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

EXECUTION

EXAMINATION

Examine lighting control devices before installation. Reject lighting control devices that are wet, moisture damaged, or mold damaged.

Examine walls and ceilings for suitable conditions where lighting control devices will be installed.

Proceed with installation only after unsatisfactory conditions have been   corrected.

SENSOR INSTALLATION

Comply with NECA 1.

Coordinate layout and installation of ceiling-mounted devices with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, smoke detectors, fire-suppression systems, and partition assemblies.

Retain paragraph below when lighting control sensors are specified.

Install and aim sensors in locations to achieve not less than 90 percent coverage of areas indicated. Do not exceed coverage limits specified in manufacturer's written instructions.

Vacancy sensors shall not be installed in any path of egress.  Occupancy/vacancy sensors shall be installed in areas per CEC.

CONTACTOR INSTALLATION

Comply with NECA 1.

Retain this article when specifying electrically held units in Part 2.

Mount electrically held lighting contactors with elastomeric isolator pads to eliminate structure-borne vibration, unless contactors are installed in an enclosure with factory-installed vibration isolators.

WIRING INSTALLATION

Coordinate this article with Drawings.

Comply with NECA 1.

Wiring Method: Comply with Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables." Minimum conduit size is 3/4 inch.

Wiring within Enclosures: Comply with NECA 1. Separate power-limited and nonpower-limited conductors according to conductor manufacturer's written instructions.

Size conductors according to lighting control device manufacturer's written instructions unless otherwise indicated.

Splices, Taps, and Terminations: Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

IDENTIFICATION

Identify components and power and control wiring according to Section 26 05 53 "Identification for Electrical Systems."

Identify controlled circuits in lighting contactors.

Identify circuits or luminaires controlled by photoelectric and occupancy sensors at each sensor.

Label time switches and contactors with a unique designation.

FIELD QUALITY CONTROL

Testing Agency: Engage a qualified testing agency to evaluate lighting control devices and perform tests and inspections prior to conducting Acceptance Testing.

Edit Acceptance Testing requirements to suit Project.  Ensure Certification forms are either on the drawings or in a separate booklet as required by DSA.

Perform the following Acceptance Tests for the lighting control system.  Testing shall be done by a technician certified by the California Energy Commission in compliance with the requirements of CBC Title 24 Part 6, California Energy Code.  Testing shall include:

Automatic Daylighting Control Acceptance.

Occupant Sensor Acceptance.

Automatic Time Switch Control Acceptance.

Demand Responsive Controls.

Outdoor Motion Sensor Acceptance.

Outdoor Lighting Shut-Off Controls.

See Section 01 40 02 "Quality Requirements, Contractor Laboratory" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

Lighting control devices will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports as required by the CCR Title 24 Part 6.  Reports shall be completed and signed by the certified technician and submitted to District and to other entities as required by the CCR Title 24 Part 6.

DEMONSTRATION

This article covers optional services; retain if Project warrants. Edit to suit Project.  Coordinate with requirements in Section 01 79 00 "Demonstration and Training." If Project includes programmable lighting controls, coordinate with system testing.

Coordinate demonstration of products specified in this Section with demonstration requirements for low-voltage, programmable lighting control systems specified in Section 26 09 43.16 "Addressable-Luminaire Lighting Controls" and Section 26 09 43.23 "Relay-Based Lighting Controls."

Engage a factory-authorized service representative to train District's maintenance personnel to adjust, operate, and maintain lighting control devices.

END OF SECTION 26 09 23

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021