MasterSpec 2013

SECTION 26 27 13

ELECTRICITY METERING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes equipment for electricity metering by District.

DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

KY Pulse: Term used by the metering industry to describe a method of measuring consumption of electricity that is based on a relay opening and closing in response to the rotation of the disk in the meter.

PC: Personal computer.

ACTION SUBMITTALS

Product Data: For each type of product indicated.

Shop Drawings: For electricity-metering equipment.

Dimensioned plans and sections or elevation layouts.

Retain subparagraph below if equipment includes wiring.

Wiring Diagrams: For power, signal, and control wiring. Identify terminals and wiring designations and color-codes to facilitate installation, operation, and maintenance. Indicate recommended types, wire sizes, and circuiting arrangements for field-installed wiring, and show circuit protection features.

INFORMATIONAL SUBMITTALS

Field quality-control reports.

Qualification Data:  For Certified Acceptance Technician.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data. In addition to items specified in Section 01 78 23 "Operation and Maintenance Data," include the following:

Hard copies of manufacturer's operating specifications, design user's guides for software and hardware, and PDF files on CD-ROM of the hard-copy Submittal.

Acceptance Testing Certification:  For load de-aggregation, provide Acceptance Testing Certification forms completed per the requirements of the CCR Title 24 Part 6.  When required, upload the acceptance forms to the State of California data electronic depository.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Certified Acceptance Technician Qualifications: A technician registered with the State of California as required by the CBC to perform de-aggregation load acceptance certification.

PROJECT CONDITIONS

Retain this article if interruption of existing electrical service is required.

Interruption of Existing Electrical Service: Do not interrupt electrical service to facilities occupied by District or others unless permitted under the following conditions and then only after arranging to provide temporary electrical service according to requirements indicated:

Notify District Construction Manager no fewer than seven days in advance of proposed interruption of electrical service.

Do not proceed with interruption of electrical service without District Construction Manager's written permission.

PRODUCTS

EQUIPMENT FOR ELECTRICITY METERING BY DISTRICT

Retain this article to specify components for District's metering. Coordinate with Drawings.

Retain this Article to comply with the CBC for load de-aggregation of electrical loads.

System Description: Able to meter designated activity loads, with or without external alarm, control, and communication capabilities, or other optional features.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Eaton Electrical Sector; Eaton Corporation.

National Meter Industries.

Square D; by Schneider Electric.

Or Equal.

General Requirements for District's Meters:

Comply with UL 1244.

Retain first subparagraph below if required by authorities having jurisdiction at Project location. Below may also be retained as a quality-control option even if not required by authorities having jurisdiction.

Meters shall be certified by California Type Evaluation Program as complying with the Part 4 CCR 4027, Article 2.2.

Enclosure: NEMA 250, [Type 1] [Type 3R] minimum, with hasp for padlocking or sealing.

Identification: Comply with requirements in Section 26 05 53 "Identification for Electrical Systems."

Memory Backup: Self-contained to maintain memory throughout power outages of 72 hours, minimum.

Nonvolatile Data Storage: kWh until reset.

Sensors: Current-sensing type, with current or voltage output, selected for optimum range and accuracy for meters indicated for this application.

Type: Split core.

Current-transformer cabinet in first subparagraph below may be required for some solid-core current sensors. Coordinate with Drawings.

Current-Transformer Cabinet: Listed or recommended by metering equipment manufacturer for use with sensors indicated.

Subparagraph below specifies an optional feature for kilowatt-hour and demand meters. Retain subparagraph to have meter provide power consumption and demand information to a building automation system to support demand-limiting action by that system. Coordinate with design of building automation system.

Interface with DDC System for HVAC: One digital KY pulse to a user-definable increment of energy measurement. Match signal to [DDC system for HVAC] <Insert signal destination> input and arrange to convey the instantaneous, integrated, demand level measured by meter to provide data for processing and possible programmed demand control action by destination system.

Kilowatt-hour Meter: Electronic [single] [three] [single- and three]-phase meters, measuring electricity used.

Voltage and Phase Configuration: Meter shall be designed for use on circuits with voltage rating and phase configuration indicated for its application.

Retain one of two subparagraphs below.

Display: LCD with characters not less than 0.25 inch high, indicating accumulative kilowatt-hours and current kilowatt load. Retain accumulated kilowatt-hour in a nonvolatile memory, until reset.

Display: Digital electromechanical counter, indicating accumulative kilowatt-hours.

The demand interval in first paragraph below should be same as used by the utility.

Kilowatt-hour/Demand Meter: Electronic [single] [three] [single- and three]-phase meters, measuring electricity use and demand. Demand shall be integrated over a [15-minute] <Insert value> interval.

Voltage and Phase Configuration: Meter shall be designed for use on circuits with voltage rating and phase configuration indicated for its application.

Display: LCD with characters not less than 0.25 inch high, indicating the following:

Accumulative kilowatt-hours

Current time and date

Current demand

Historic peak demand

Time and date of historic peak demand

Retain accumulated kilowatt-hour and historic peak demand in a nonvolatile memory, until reset.

Data Transmission Cable: Transmit KY pulse data over Class 1 control-circuit conductors in raceway. Comply with Section 27 15 00 "Communications Horizontal Cabling."

RESETTABLE CUSTOMER SERVICE METER

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Eaton Electrical Sector; Eaton Corporation.

National Meter Industries.

Square D; by Schneider Electric.

Or Equal.

Meter Characteristics:

Meter shall be designed for Multifunction Electrical Measurement on 3 phase power systems. The Meter shall support 3-Element Wye, 2.5 Element Wye, 2 Element Delta, 4 wire Delta systems.

Meter surge withstand shall conform to IEEE C37.90.1 and ANSI C62.41 (6KV).

Meter shall be user programmable for voltage range to any PT ratio.

Meter shall have a burden of up to .36VA per phase, Max at 600V, 0.014VA at 120 Volts.

Meter shall accept a direct voltage input range of up to 576 Volts Line to Neutral, and a range of up to 721 Volts Line to Line.

Meter shall accept a current input of up to 10 amps continuous.  Startup current for a 5 Amp input shall be no greater than .005 Amps.

Meters shall provide voltage per phase, amperes, instantaneous kW demand, historical peak kW demand, kWh, kWh per rate period, PF, and kVAR.  The kWh shall be resettable by the user.

Provide current transformers consistent with the system voltage and with the ratio indicated on the   Drawings.

EXECUTION

INSTALLATION

Comply with equipment installation requirements in NECA 1.

IDENTIFICATION

Comply with requirements for identification specified in Section 26 05 53 "Identification for Electrical Systems."

Series Combination Warning Label: Self-adhesive type, with text as required by NFPA 70.

Equipment Identification Labels: Adhesive film labels with clear protective overlay.

FIELD QUALITY CONTROL

Perform tests and inspections.

Tests and Inspections:

As required by the CBC AND CEC Title 24.

The Certified Acceptance Technician shall complete and sign the certification documents on the Drawings or in the Specifications and submit to the Project Inspector.

See Section 01 40 02 "Quality Requirements, Contractor Laboratory" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

Electricity metering will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

END OF SECTION 26 27 13

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021