MasterSpec 12/16

SECTION 26 27 26

WIRING DEVICES

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

B.      Refer to Section 26 09 23 “Lighting Control Devices” for lighting control requirements

including occupancy/vacancy sensors, photoelectric switches, digital time switches,

daylight harvesting controllers and system room controllers.

C. Refer to Section 26 05 53 “Identification for Electrical Systems” for labeling of device cover             plates.

SUMMARY

Section Includes:

Standard-grade receptacles 125 V, 20 A.

GFCI receptacles 125 V, 20 A.

Twist-locking receptacles.

Pendant cord-connector devices.

Cord and plug sets.

Toggle switches 120/277 V, 20 A.

Occupancy sensors.

Decorator-style convenience.

Digital timer light switches.

Wall plates.

Floor service outlets.

Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 26 05 53 “Identification for Electrical Systems” for labeling of device cover plates.

Section 26 09 23 “Lighting Control Devices” for lighting control requirements including occupancy/vacancy sensors, photoelectric switches, digital time switches, daylight harvesting controllers and system room controllers.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

EMI: Electromagnetic interference.

GFCI: Ground-fault circuit interrupter.

Pigtail: Short lead used to connect a device to a branch-circuit conductor.

RFI: Radio-frequency interference.

ACTION SUBMITTALS

Product Data: For each type of product.

Shop Drawings: List of legends and description of materials and process used for premarking wall plates.

INFORMATIONAL SUBMITTALS

Field quality-control reports.

PRODUCTS

GENERAL WIRING-DEVICE REQUIREMENTS

Wiring Devices, Components, and Accessories: Listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

Comply with CEC.

Comply with NEMA WD 1.

Devices for District-Furnished Equipment:

Receptacles: Match plug configurations.

Retain "Cord and Plug Sets" Subparagraph below if retaining "Cord and Plug Sets" Article.

Cord and Plug Sets: Match equipment requirements.

Device Color:

Retain "Wiring Devices Connected to Normal Power System" Subparagraph below unless colors are indicated or scheduled on Drawings. If retaining below, revise title if a separate emergency power system serving wiring devices is not provided.

Wiring Devices Connected to Normal Power System:  [Ivory] [White] <Insert color> unless otherwise indicated or required by CEC or device listing.

Retain "Wiring Devices Connected to Essential Electrical System" Subparagraph below if a separate emergency power system serving wiring devices is required.

Source Limitation:  Obtain each type of wiring device and associated wall plate from single source from single manufacturer.

Occupancy Control Receptacles:  Provide identification as required by CCR Title 24 Part 6.

STRAIGHT-BLADE RECEPTACLES

Duplex Receptacles, 125 V, 20 A:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or Equal.

Description: Two pole, three wire, and self-grounding.

Configuration: NEMA WD 6, Configuration 5-20R.

Standards: Comply with UL 498 and FS W-C-596.

Grade: Heavy duty.

Occupancy Controlled Receptacles, 125 V, 20 A:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or equal.

Description: Two pole, three wire, and self-grounding.

Configuration: NEMA WD 6, Configuration 5-20R.

Standards: Comply with UL 498 and FS W-C-596.

Grade: Heavy duty.

Engraved markings indicating the controlled position, either split wired or for the complete duplex receptacle.

Tamper- Resistant Convenience Receptacles, 125 V, 20 A:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or Equal.

Description: Two pole, three wire, and self-grounding. Integral shutters that operate only when a plug is inserted in the receptacle.

Configuration: NEMA WD 6, Configuration 5-20R.

Standards: Comply with UL 498 and FS W-C-596.

"Marking" Subparagraph below requires compliance with NFPA 70, Article 406.12.

Marking: Listed and labeled as complying with CEC, "Tamper-Resistant Receptacles" Article.

GFCI RECEPTACLES 125 V, 20 A

Duplex GFCI  Receptacles, 125 V, 20 A:  Heavy-Duty Specification Grade.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or equal.

Description: Integral GFCI with "Test" and "Reset" buttons and LED indicator light. Two pole, three wire, and self-grounding.

Configuration: NEMA WD 6, Configuration 5-20R.

Non-feed-through-type GFCI unit shall be selected where no protection of downstream receptacles is required.

Type: [Feed] [Non-feed] through.

Standards: Comply with UL 498, UL 943 Class A, and FS W-C-596.

Tamper-Resistant GFCI  Receptacles, 125 V, 20 A:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or equal.

Description: Integral GFCI with "Test" and "Reset" buttons and LED indicator light. Two pole, three wire, and self-grounding. Integral shutters that operate only when a plug is inserted in the receptacle.

Configuration: NEMA WD 6, Configuration 5-20R.

Type: [Feed] [Non-feed] through.

Standards: Comply with UL 498, UL 943 Class A, and FS W-C-596.

"Marking" Subparagraph below requires compliance with CEC, Article 406.12.

Marking: Listed and labeled as complying with CEC, "Tamper-Resistant Receptacles" Article.

TWIST-LOCKING RECEPTACLES

Single Convenience Receptacles, 125 V, 20 A:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or Equal.

Configuration: NEMA WD 6, Configuration L5-20R.

Standards: Comply with UL 498

Grade: Heavy duty.

Single Convenience Receptacles, 250 V, 20 A:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or Equal.

Configuration: NEMA WD 6, Configuration L6-20R.

Standards: Comply with UL 498

Grade: Heavy duty.

PENDANT CORD-CONNECTOR DEVICES

Description: Matching, locking-type plug and receptacle body connector, heavy duty grade.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Premise Wiring.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or Equal.

Revise NEMA configuration in "Configuration" Paragraph below to suit Project.

Configuration: NEMA WD 6, Configurations L5-20P and L5-20R.

Body: Nylon, with screw-open, cable-gripping jaws and provision for attaching external cable grip.

Delete "External Cable Grip" Paragraph below if not required.

External Cable Grip: Woven wire-mesh type made of high-strength, galvanized-steel wire strand, matched to cable diameter, and with attachment provision designed for corresponding connector.

Standards: Comply with FS W-C-596.

CORD AND PLUG SETS

Retain this article if cord and plug sets for equipment are furnished by District or are specified in other Sections. Coordinate with other Sections and with Part 3.

Match voltage and current ratings and number of conductors to requirements of equipment being connected.

Cord: Rubber-insulated, stranded-copper conductors, with Type SOW-A jacket; with green-insulated grounding conductor and ampacity of at least 130 percent of the equipment rating.

Plug: Nylon body and integral cable-clamping jaws. Match cord and receptacle type for connection.

TOGGLE SWITCHES

Single-Pole Switches, 120/277 V, 20 A, Heavy-Duty Specification Grade:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or equal.

Standards: Comply the UL 20 and FS-W-S 896

Grade: Heavy duty.

Two Pole Switches 120/277 V, 20 A

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

Pass & Seymour/Legrand (Pass & Seymour).

Or equal.

Standards: Comply the UL 20 and FS-W-S 896

Grade: Heavy duty.

OCCUPANCY SENSORS

Each manufacturer's switch rating is different, but rated design values are generally not less than 800-VA fluorescent at 120 V, and 1200-VA fluorescent at 277 V, and 800-W incandescent.

Adaptive technology includes the ability to sense and memorize usage patterns in the space and help eliminate false offs.

Coordinate below with Section 26 09 23 Lighting Control Devices.

Wall Switch Sensors Light Switch, Dual Technology:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

WattStopper.

Or Equal.

Description:  Switchbox-mounted, combination lighting-control sensor and conventional switch lighting-control unit using dual (ultrasonic and passive infrared) technology.

Standards: Comply with UL 20.

Verify electrical characteristics with manufacturer. For low-voltage systems, delete first subparagraph below and insert requirements for low-voltage system.

Rated 960 W at 120 V ac for tungsten lighting, 10 A at 120 V ac or 10 A at 277 V ac for fluorescent or LED lighting, and 1/4 hp at 120 V ac.

Adjustable time delay of [five] [10] [15] [20] minutes.

"Automatic-On" mode turns on lights when motion is sensed. "Manual-On" mode requires that the switch be depressed to turn on lights. Both modes use motion sensing to keep lights on.

Able to be locked to [Automatic] [Manual]-On mode.

Automatic Light-Level Sensor: Adjustable from 2 to 200 fc.

Retain one of three "Connections" subparagraphs below.

Connections: Provisions for connection to BAS.

Connections: RJ-45 communications outlet.

Connections: Integral wireless networking.

Exterior Occupancy Sensors:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Incorporated; Wiring Device-Kellems.

Leviton Manufacturing Co., Inc.

WattStopper.

Or Equal.

Description:  Commercial grade, passive-infrared type, 120/277 V, weatherproof, adjustable time delay up to 15 minutes, 180-degree field of view, and 110-foot detection range.  Minimum switch rating: 1000-W incandescent, 500-VA fluorescent.

WALL PLATES

Single Source: Obtain wall plates from same manufacturer of wiring devices.

Single and combination types shall match corresponding wiring devices.

Plate-Securing Screws: Metal with head color to match plate finish.

Material for Finished Spaces: 0.035-inch-thick, satin-finished, Type 302 stainless steel.

Material for Unfinished Spaces: Galvanized steel.

Material for Damp Locations: Cast aluminum with spring-loaded lift cover, and listed and labeled for use in wet and damp locations.

Wet-Location, Weatherproof Cover Plates: NEMA 250, complying with Type 3R, weather-resistant, die-cast aluminum with lockable cover.

FLOOR SERVICE FITTINGS

Service fittings in "Type" Paragraphs below are available for voice and data communication cabling as well as for power.

Flush-Type Floor Service Fitting:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hubbell Premise Wiring.

Thomas & Betts Power Solutions; ABB Group.

Wiremold / Legrand.

Or Equal.

Description: Type: Modular, flush-type, dual-service units suitable for wiring method used, with cover flush with finished floor.

Compartments: Barrier separates power from voice and data communication cabling.

Service Plate and Cover: [Rectangular] [Round], [die-cast aluminum] [solid brass] with satin finish.

Power Receptacle: NEMA WD 6 Configuration 5-20R, gray finish, unless otherwise indicated.

Data Communication Outlet: [Blank cover with bushed cable opening.] [Two modular, keyed, color-coded, RJ-45 jacks for twisted pair cable, complying with requirements in Section 271513 "Communications Copper Horizontal Cabling."]

FINISHES

Device Color:

Retain "Wiring Devices Connected to Normal Power System" Subparagraph below unless colors are indicated or scheduled on Drawings.

Wiring Devices Connected to Normal Power System: [Ivory] [White] <Insert color> unless otherwise indicated or required by CEC or device listing.

Wall Plate Color: 0.035-inch-thick, satin-finished, Type 302 stainless steel.

EXECUTION

INSTALLATION

Show mounting heights in the Drawings per DSA requirements.

Comply with NECA 1, including mounting heights listed in that standard or per the CEC unless otherwise noted on Drawings.

Coordination with Other Trades:

Protect installed devices and their boxes. Do not place wall finish materials over device boxes and do not cut holes for boxes with routers that are guided by riding against outside of boxes.

Keep outlet boxes free of plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other material that may contaminate the raceway system, conductors, and cables.

Install device boxes in brick or block walls so that the cover plate does not cross a joint unless the joint is troweled flush with the face of the wall.

Install wiring devices after all wall preparation, including painting, is complete.

Conductors:

Do not strip insulation from conductors until right before they are spliced or terminated on devices.

Strip insulation evenly around the conductor using tools designed for the purpose. Avoid scoring or nicking of solid wire or cutting strands from stranded wire.

The length of free conductors at outlets for devices shall meet provisions of CEC, Article 300, without pigtails.

Existing Conductors:

Cut back and pigtail, or replace all damaged conductors.

Straighten conductors that remain and remove corrosion and foreign matter.

Pigtailing existing conductors is permitted, provided the outlet box is large enough.

Device Installation:

Replace devices that have been in temporary use during construction and that were installed before building finishing operations were complete.

Keep each wiring device in its package or otherwise protected until it is time to connect conductors.

Do not remove surface protection, such as plastic film and smudge covers, until the last possible moment.

Connect devices to branch circuits using pigtails that are not less than 6 inches in length.

When there is a choice, use side wiring with binding-head screw terminals. Wrap solid conductor tightly clockwise, two-thirds to three-fourths of the way around terminal screw.

Use a torque screwdriver when a torque is recommended or required by manufacturer.

When conductors larger than No. 12 AWG are installed on 15- or 20-A circuits, splice No. 12 AWG pigtails for device connections.

Tighten unused terminal screws on the device.

When mounting into metal boxes, remove the fiber or plastic washers used to hold device-mounting screws in yokes, allowing metal-to-metal contact.

Receptacle Orientation:

Install ground pin of vertically mounted receptacles up, and on horizontally mounted receptacles to the left.

Device Plates: Do not use oversized or extra-deep plates. Repair wall finishes and remount outlet boxes when standard device plates do not fit flush or do not cover rough wall opening.

Dimmers:

Install dimmers within terms of their listing.

Verify that dimmers used for fan speed control are listed for that application.

Install unshared neutral conductors on line and load side of dimmers according to manufacturers' device listing conditions in the written instructions.

Coordinate both paragraphs below with Drawings.

Arrangement of Devices: Unless otherwise indicated, mount flush, with long dimension vertical and with grounding terminal of receptacles on top. Group adjacent switches under single, multigang wall plates.

Adjust locations of floor service outlets and service poles to suit arrangement of partitions and furnishings.

Do not install vacancy sensors in any path of egress.  Install occupancy/vacancy sensors in areas per the latest edition of CEC Title 24

GFCI RECEPTACLES

Install non-feed-through-type GFCI receptacles where protection of downstream receptacles is not required.

IDENTIFICATION

Comply with Section 26 05 53 "Identification for Electrical Systems."

Receptacle and Light Switch Cover Plates:  Engraved or silk screened with panel and circuit number identified for each device.

FIELD QUALITY CONTROL

Test Instruments: Use instruments that comply with UL 1426.

Test Instrument for Convenience Receptacles: Digital wiring analyzer with digital readout or illuminated digital-display indicators of measurement.

Tests for Receptacles:

Line Voltage: Acceptable range is 105 to 132 V.

Percent Voltage Drop under 15-A Load: A value of 6 percent or higher is unacceptable.

Ground Impedance: Values of up to 2 ohms are acceptable.

GFCI Trip: Test for tripping values specified in UL 1436 and UL 943.

Using the test plug, verify that the device and its outlet box are securely mounted.

Tests shall be diagnostic, indicating damaged conductors, high resistance at the circuit breaker, poor connections, inadequate fault current path, defective devices, or similar problems. Correct circuit conditions, remove malfunctioning units and replace with new ones, and retest as specified above.

See Section 01 40 02 "Quality Requirements, Contractor Laboratory" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

Wiring device will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

END OF SECTION 26 27 26

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021