MasterSpec 2013

SECTION 26 28 13

FUSES

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Cartridge fuses rated 600 V ac and less for use in the following:

Control circuits.

Enclosed controllers.

Enclosed switches.

Spare-fuse cabinets.

Related Requirements:

Section 26 13 23 “Medium-Voltage, Metal-enclosed Switchgear” for medium voltage fuses.

ACTION SUBMITTALS

Product Data: For each type of product. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for spare-fuse cabinets. Include the following for each fuse type indicated:

Retain "Ambient Temperature Adjustment Information" Subparagraph if variations in fuse performance due to ambient temperature extremes can affect system performance.

Ambient Temperature Adjustment Information: If ratings of fuses have been adjusted to accommodate ambient temperatures, provide list of fuses with adjusted ratings.

For each fuse having adjusted ratings, include location of fuse, original fuse rating, local ambient temperature, and adjusted fuse rating.

Provide manufacturer's technical data on which ambient temperature adjustment calculations are based.

Dimensions and manufacturer's technical data on features, performance, electrical characteristics, and ratings.

Retain subparagraph below if Project includes elevators and fused elevator shunt-trip switches.

Fuse sizes for elevator feeders and elevator disconnect switches.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For fuses to include in emergency, operation, and maintenance manuals. In addition to items specified in Section 01 77 00 "Closeout Procedures," include the following:

Ambient temperature adjustment information.

Current-limitation curves for fuses with current-limiting characteristics.

Time-current coordination curves (average melt) and current-limitation curves (instantaneous peak let-through current) for each type and rating of fuse used on the Project. Submit in PDF format.

Coordination charts and tables and related data.

FIELD CONDITIONS

Where ambient temperature to which fuses are directly exposed is less than 40 deg F or more than 100 deg F, apply manufacturer's ambient temperature adjustment factors to fuse ratings.

PRODUCTS

MANUFACTURERS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Cooper Bussmann; a division of Cooper Industries.

Littelfuse, Inc.

Mersen USA.

Or Equal.

Source Limitations: Obtain fuses, for use within a specific product or circuit, from single source from single manufacturer.

CARTRIDGE FUSES

Fuse "Class" defines fuse performance category, including interrupting rating. Include current rating and class for cartridge fuses either on Drawings or in "Fuse Applications" Article.

Characteristics: NEMA FU 1, current-limiting, nonrenewable cartridge fuses with voltage ratings consistent with circuit voltages.

Use Type RK-1 fuses for feeders.  Do not use RK-1 fuses with District “2000HVAC” units due to multiple failures District-wide.  Use RK-5 fuses in these applications.  Work with assigned District Project Manager to coordinate with Physical Plant Operations personnel.

Use Type RK-5 fuses for all motor loads.

Type RK-5: [250] [600]-V, zero- to 600-A rating, 200 kAIC[, time delay].

Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Comply with NEMA FU 1 for cartridge fuses.

Comply with NFPA 70.

Coordinate fuse ratings with utilization equipment nameplate limitations of maximum fuse size and with system short-circuit current levels.

SPARE-FUSE CABINET

Characteristics: Wall-mounted steel unit with full-length, recessed piano-hinged door and key-coded cam lock and pull.

Size: Adequate for storage of spare fuses specified with [15] <Insert number> percent spare capacity minimum.

Finish: Gray, baked enamel.

Identification: "SPARE FUSES" in 1-1/2-inch-high letters on exterior of door.

Fuse Pullers: For each size of fuse, where applicable and available, from fuse manufacturer.

EXECUTION

EXAMINATION

Examine fuses before installation. Reject fuses that are moisture damaged or physically damaged.

Examine holders to receive fuses for compliance with installation tolerances and other conditions affecting performance, such as rejection features.

Examine utilization equipment nameplates and installation instructions. Install fuses of sizes and with characteristics appropriate for each piece of equipment.

Evaluate ambient temperatures to determine if fuse rating adjustment factors must be applied to fuse ratings.

Proceed with installation only after unsatisfactory conditions have been corrected.

FUSE APPLICATIONS

Retain this article if fuse class and type designations are not indicated on Drawings. Indicate fuse ampere ratings on Drawings. Retain fuse classes and types by coordinating required average melt characteristics and peak let-through currents with Section 26 05 73.16 "Coordination Studies."

In small systems, the fuse characteristics might be shown on the system single-line diagram. In larger or more complex systems, a separate fuse application chart would be more advantageous.

Cartridge Fuses:

Class T fuses in "Service Entrance" Subparagraph are normally used in main switches ahead of meter banks because of their compact size and excellent current-limiting characteristics. Their current-limiting feature often allows using circuit breakers with 10-kA interrupting rating at tenant meters.

Multiple fuse types might be specified for an application from the following types for a single project. If more than one class is selected for any of the following applications, indicate on the Drawings which class is required for each fuse of that application type. Consider using a chart to clearly indicate usage.

Service Entrance: [Class L, fast acting] [Class L, time delay] [Class RK5, time delay] [Class J, fast acting] [Class J, time delay] [Class T, fast acting].

Feeders: [Class L, fast acting] [Class L, time delay] [Class RK1, fast acting] [Class RK1, time delay] [Class RK5, fast acting] [Class RK5, time delay] [Class J, fast acting] [Class J, time delay].

Motor Branch Circuits:  Class RK5, time delay.

Large Motor Branch (601-4000 A): Class L, time delay.

Power Electronics Circuits: [Class J, high speed] [Class T, fast acting].

If retaining subparagraph below, verify open indication is available in the fuse type or fuse covers included in the Specifications. If indication is desired for some fuse types and not others, include a list of fuses that require indication.

Provide open-fuse indicator fuses or fuse covers with open fuse indication.

INSTALLATION

Install fuses in fusible devices. Arrange fuses so rating information is readable without removing fuse.

Install spare-fuse cabinet(s) in location shown on the Drawings or as indicated in the field by District Construction Manager.

IDENTIFICATION

Install labels complying with requirements for identification specified in Section 26 05 53 "Identification for Electrical Systems" and indicating fuse replacement information inside of door of each fused switch and adjacent to each fuse block, socket, and holder.

END OF SECTION 26 28 13

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021