MasterSpec 2011

SECTION 26 43 13

SURGE PROTECTION FOR LOW-VOLTAGE ELECTRICAL POWER CIRCUITS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes field-mounted SPDs for low-voltage (120 to 600 V) power distribution and control equipment.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 26 24 13 "Switchboards" for factory-installed SPDs.

Section 26 24 16 "Panelboards" for factory-installed SPDs.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

Inominal: Nominal discharge current.

MCOV: Maximum continuous operating voltage.

Mode(s), also Modes of Protection: The pair of electrical connections where the VPR applies.

MOV: Metal-oxide varistor; an electronic component with a significant non-ohmic current-voltage characteristic.

OCPD: Overcurrent protective device.

SCCR: Short-circuit current rating.

SPD: Surge protective device.

VPR: Voltage protection rating.

ACTION SUBMITTALS

Product Data: For each type of product.

Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Copy of UL Category Code VZCA certification, as a minimum, listing the tested values for VPRs, Inominal ratings, MCOVs, type designations, OCPD requirements, model numbers, system voltages, and modes of protection.

INFORMATIONAL SUBMITTALS

Field quality-control reports.

Sample Warranty: For manufacturer's special warranty.

CLOSEOUT SUBMITTALS

Maintenance Data: For SPDs to include in maintenance manuals.

WARRANTY

Manufacturer's Warranty: Manufacturer agrees to replace or replace SPDs that fail in materials or workmanship within specified warranty period.

Warranty Period: Five years from date of Substantial Completion.

PRODUCTS

GENERAL SPD REQUIREMENTS

SPD with Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Comply with NFPA 70.

Comply with UL 1449.

MCOV of the SPD shall be the nominal system voltage.

SERVICE ENTRANCE SUPPRESSOR

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Advanced Protection Technologies Inc. (APT).

Eaton.

Liebert; a brand of Emerson Electric Co.

Or Equal.

Retain one of two "SPDs" paragraphs below.

SPDs: Comply with UL 1449, [Type 1] [Type 2].

SPDs: Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 1449, [Type 1] [Type 2]

SPDs with the following features and accessories:

Retain first subparagraph below when specifying Type 1 SPD to be installed ahead of the service disconnect, when this disconnect is installed to facilitate maintenance.

Integral disconnect switch.

Retain first subparagraph below to disconnect the SPD when low-current, high-impedance faults occur.

Internal thermal protection that disconnects the SPD before damaging internal suppressor components.

Indicator light display for protection status.

The 5 A and 250-V ac rating of the Form-C contacts is suitable for remote annunciators using Class 1 control circuits. Insert other ratings when monitoring is performed by Ethernet communications protocol used by building power monitoring and control system.

Form-C contacts rated at [5 A and 250-V ac] [2 A and 24-V ac], one normally open and one normally closed, for remote monitoring of protection status.[ Contacts shall reverse on failure of any surge diversion module or on opening of any current-limiting device. Coordinate with building power monitoring and control system.]

Surge counter.

Retain first paragraph below to require Type 2 SPDs to be co-listed as electromagnetic and radio-frequency interference filters.

Comply with UL 1283.

Generally available surge current ratings are 300, 250, 200, 150, and 100 kA.

Peak Surge Current Rating: The minimum single-pulse surge current withstand rating per phase shall not be less than [200 kA] [240kA] [320 kA] [480 kA]. The peak surge current rating shall be the arithmetic sum of the ratings of the individual MOVs in a given mode.

Retain one of first two paragraphs below. Verify compatibility of peak surge current rating and VPR.

Protection modes and UL 1449 VPR for grounded wye circuits with [480Y/277 V] [208Y/120 V], three-phase, four-wire circuits shall not exceed the following:

Line to Neutral: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

Line to Ground: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

Line to Line: [2000 V for 480Y/277 V] [1000 V for 208Y/120 V].

Protection modes and UL 1449 VPR for 240/120 V, single-phase, three-wire circuits shall not exceed the following:

Line to Neutral: 700 V.

Line to Ground: [700 V] [1000 V].

Line to Line: 1000 V.

SCCR: Equal or exceed [100 kA] [200 kA].

Inominal Rating: 20 kA.

PANEL SUPPRESSORS

Retain this article for SPDs other than those installed at the service entrance. SPD described in this article is required by NFPA 70 to be installed with OCPD. The type and size of OCPD depends on the UL listing requirements.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Advanced Protection Technologies Inc. (APT).

Eaton.

Liebert; a brand of Emerson Electric Co.

Or Equal.

SPDs: Comply with UL 1449, [Type 1] [Type 2].

Include LED indicator lights for power and protection status.

Retain first subparagraph below to disconnect the SPD when low-current, high-impedance faults occur.

Internal thermal protection that disconnects the SPD before damaging internal suppressor components.

Include Form-C contacts rated at 5 A and 250-V ac, one normally open and one normally closed, for remote monitoring of protection status.[ Contacts shall reverse on failure of any surge diversion module or on opening of any current-limiting device. Coordinate with building power monitoring and control system.]

Generally available surge current ratings are 300, 250, 200, 150, and 100 kA.

Peak Surge Current Rating: The minimum single-pulse surge current withstand rating per phase shall not be less than [100 kA]. The peak surge current rating shall be the arithmetic sum of the ratings of the individual MOVs in a given mode.

Retain first paragraph below to require Type 2 SPDs to be co-listed as electromagnetic and radio-frequency interference filters.

Comply with UL 1283.

Retain one of first two paragraphs below. Verify compatibility of peak surge current rating and clamping voltage. Reference to UL 1449 is to its third edition.

Protection modes and UL 1449 VPR for grounded wye circuits with [480Y/277 V] [208Y/120 V], three-phase, four-wire circuits shall not exceed the following:

Line to Neutral: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

Line to Ground: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

Neutral to Ground: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

Line to Line: [2000 V for 480Y/277 V] [1200 V for 208Y/120 V]

Protection modes and UL 1449 VPR for 240/120-V, single-phase, three-wire circuits shall not exceed the following:

Line to Neutral: 700 V.

Line to Ground: 700 V.

Neutral to Ground: 700 V.

Line to Line: 1200 V.

SCCR: Equal or exceed [100 kA] [200 kA].

Inominal Rating: [20 kA] [10 kA].

ENCLOSURES

Indoor Enclosures: NEMA 250, Type 1.

Outdoor Enclosures: NEMA 250, [Type 3R] [Type 4].

CONDUCTORS AND CABLES

Retain this article when SPD accessories are connected to remote indicators or when interfacing with building management system.

Power Wiring: Same size as SPD leads, complying with Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

Class 2 Control Cables: Multiconductor cable with copper conductors not smaller than No. 18 AWG, complying with Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

Class 1 Control Cables: Multiconductor cable with copper conductors not smaller than No. 14 AWG, complying with Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

EXECUTION

INSTALLATION

Comply with NECA 1.

Install an OCPD or disconnect as required to comply with the UL listing of the SPD.

Install SPDs with conductors between suppressor and points of attachment as short and straight as possible, and adjust circuit-breaker positions to achieve shortest and straightest leads. Do not splice and extend SPD leads unless specifically permitted by manufacturer. Do not exceed manufacturer's recommended lead length. Do not bond neutral and ground.

Use crimped connectors and splices only. Wire nuts are unacceptable.

Wiring:

Power Wiring: Comply with wiring methods in Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

Controls: Comply with wiring methods in Section 26 05 19 "Low-Voltage Electrical Power Conductors and Cables."

FIELD QUALITY CONTROL

Perform the following tests and inspections with the assistance of a factory-authorized service representative.

Compare equipment nameplate data for compliance with Drawings and Specifications.

Inspect anchorage, alignment, grounding, and clearances.

Verify that electrical wiring installation complies with manufacturer's written installation requirements.

See Section 01 40 02 "Quality Requirements, Contractor Laboratory" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

An SPD will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

STARTUP SERVICE

Complete startup checks according to manufacturer's written instructions.

Do not perform insulation-resistance tests of the distribution wiring equipment with SPDs installed. Disconnect SPDs before conducting insulation-resistance tests, and reconnect them immediately after the testing is over.

Energize SPDs after power system has been energized, stabilized, and tested.

DEMONSTRATION

Engage a factory-authorized service representative to train District’s maintenance personnel to operate and maintain SPDs.

END OF SECTION 26 43 13

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021