MasterSpec 2014

SECTION 27 05 26

GROUNDING AND BONDING FOR COMMUNICATIONS SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

CEC and IEEE C2 include basic grounding requirements for electrical safety. This Section supplements those requirements with grounding requirements for communications systems and with optional grounding methods and materials for power and electronic systems that go beyond basic minimum safety requirements.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Grounding conductors.

Grounding connectors.

Grounding busbars.

Grounding rods.

Grounding labeling.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

BBC: Backbone Bonding Conductor.

EMT: Electrical metallic tubing.

PBB:  Primary Bonding Busbar.

RBB: Rack Bonding Busbar.

RCDD: Registered Communications Distribution Designer.

SBB: Secondary Bonding Busbar.

TBB: Telcommunications Bonding Backbone.

TBC: Telecommunications Bonding Conductor.

TEBC: Telecommunications Equipment Bonding Conductor.

ACTION SUBMITTALS

Product Data: For each type of product.

Shop Drawings: For communications equipment room signal reference grid. Include plans, elevations, sections, details, and attachments to other work.

INFORMATIONAL SUBMITTALS

Retain "As-Built Data" Paragraph below to require Contractor to provide Drawings that locate significant grounding features. Section 01 78 23 "Operation and Maintenance Data" and Section 01 78 39 "Project Record Documents" require submittals to be included in those documents for use by maintenance forces throughout the life of Project.

As-Built Data: Plans showing as-built locations of grounding and bonding infrastructure, including the following:

BBCs, PBBs, RBBs, SBBs, TBBs, TBCs, and routing of their bonding conductors.

Coordinate two "Qualification Data" paragraphs below with qualification requirements in "Quality Assurance" Article.

Qualification Data: For [Installer, ]installation supervisor, and field inspector.

Qualification Data: For testing agency and testing agency's field supervisor.

Field quality-control reports.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For grounding to include in emergency, operation, and maintenance manuals.

In addition to items specified in Section 01 78 23 "Operation and Maintenance Data," include the following:

Result of the ground-resistance test, measured at the point of BBC connection.

Result of the bonding-resistance test at each PBB, SBB, RBB, and its nearest grounding electrode.

Include recommended testing intervals.

QUALITY ASSURANCE

Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

Installation Supervision: Installation shall be under the direct supervision of ITS [Technician] [Installer 2], who shall be present at all times when Work of this Section is performed at Project site.

Field Inspector: Currently registered by BICSI as [RCDD] [ITS Installer 2] to perform the on-site inspection.

PRODUCTS

SYSTEM COMPONENTS

Comply with ANSI/TIA-607-C.

CONDUCTORS

Comply with UL 486A-486B.

Insulated Conductors: Stranded copper wire, green or green with yellow stripe insulation, insulated for 600 V, and complying with UL 83.

Ground wire for custom-length equipment ground jumpers shall be No. 6 AWG, 19-strand, UL-listed, Type THHN wire.

Retain "Cable Tray Equipment Grounding Wire" Subparagraph below if an equipment grounding conductor is required. If the ground wire serves as the telecommunications bonding backbone, indicate wire size on Drawings.

If cable tray contains electrical power conductors, then CEC, Article 392 "Cable Trays" governs, and the minimum equipment grounding conductor size is No. 4 AWG.

Cable Tray Equipment Grounding Wire: No. 6 AWG.

Cable Tray Grounding Jumper:

Not smaller than No. 6 AWG and not longer than 12 inches. If jumper is a wire, it shall have a crimped grounding lug with two holes and long barrel for two crimps. If jumper is a flexible braid, it shall have a one-hole ferrule. Attach with grounding screw or connector provided by cable tray manufacturer.

CONNECTORS

Irreversible connectors listed for the purpose. Listed by an NRTL as complying with CEC for specific types, sizes, and combinations of conductors and other items connected. Comply with UL 486A-486B.

Compression Wire Connectors: Crimp-and-compress connectors that bond to the conductor when the connector is compressed around the conductor. Comply with UL 467.

Electroplated tinned copper, C and H shaped.

Busbar Connectors: Cast silicon bronze, solderless compression-type, mechanical connector; with a long barrel and two holes spaced on 5/8- or 1-inch centers for a two-bolt connection to the busbar.

Welded Connectors: Exothermic-welding kits of types recommended by kit manufacturer for materials being joined and installation conditions.

GROUNDING BUSBARS

PBB: Predrilled, wall-mounted, rectangular bars of hard-drawn solid copper, [1/4 by 4 inches] in cross section, length as indicated on Drawings. The busbar shall be NRTL listed for use as PBB and shall comply with ANSI/TIA-607-C.

Predrilling shall be with holes for use with lugs specified in this Section.

Mounting Hardware: Stand-off brackets that provide a minimum 2-inch separation from the wall.

Stand-off insulators for mounting shall be Lexan or PVC. Comply with UL 891 for use in 600-V switchboards, impulse tested at 5000 V.

SBB: Predrilled rectangular bars of hard-drawn solid copper, [1/4 by 4 inches] in cross section, length as indicated on Drawings. The busbar shall be for wall mounting, shall be NRTL listed as complying with UL 467, and shall comply with ANSI/TIA-607-C.

Predrilling shall be with holes for use with lugs specified in this Section.

Mounting Hardware: Stand-off brackets that provide a minimum 2-inch separation from the wall.

Stand-off insulators for mounting shall be Lexan or PVC. Comply with UL 891 for use in 600-V switchboards, impulse tested at 5000 V.

Retain "Rack and Cabinet Grounding Busbars" Paragraph below if equipment cabinets and racks are not specified with grounding busbars.

RBB: Rack and Cabinet Grounding Busbars: Rectangular bars of hard-drawn solid copper, accepting conductors ranging from No. 14 to No. 2/0 AWG, NRTL listed as complying with UL 467, and complying with ANSI/TIA-607-C. Predrilling shall be with holes for use with lugs specified in this Section.

Cabinet-Mounted Busbar: Terminal block, with stainless-steel or copper-plated hardware for attachment to the cabinet.

Rack-Mounted Horizontal Busbar: Designed for mounting in 19- or 23-inch equipment racks. Include a copper splice bar for transitioning to an adjoining rack, and stainless-steel or copper-plated hardware for attachment to the rack.

Rack-Mounted Vertical Busbar: 72 or 36 inches stainless-steel or copper-plated hardware for attachment to the rack.

GROUND RODS

Retain this article if ground rods incidental to ground rings and duct banks are required. Indicate ground rod locations and connections on Drawings.

The installation of grounding electrode system for the alternating-current (ac) power system, which includes ground rods, ground rings, metal underground water pipes, metal building frames, concrete-encased electrodes, and pipe and plate electrodes, is specified in Section 26 05 26 "Grounding and Bonding for Electrical Systems." The grounding and bonding system of this Section is connected to the grounding and bonding of the ac power system with the TBC from the PBB specified in "Grounding Electrode System" Article.

Ground Rods: [Copper-clad] [Zinc-coated] [Stainless-] steel[, sectional type]; [3/4 inch by 10 feet] [5/8 by 96 inches] in diameter.

IDENTIFICATION

Comply with requirements for identification products in Section 27 05 53 "Identification for Communications Systems."

EXECUTION

EXAMINATION

Examine the ac grounding electrode system and equipment grounding for compliance with requirements for maximum ground-resistance level and other conditions affecting performance of grounding and bonding of the electrical system.

Inspect the test results of the ac grounding system measured at the point of TBC connection.

Prepare written report, endorsed by Installer, listing conditions detrimental to performance of the Work.

Proceed with connection of the TBC only after unsatisfactory conditions have been corrected.

INSTALLATION

Bonding shall include the ac utility power service entrance, the communications cable entrance, and the grounding electrode system. The bonding of these elements shall form a loop so that each element is connected to at least two others.

Comply with NECA 1.

Comply with ANSI/TIA-607-C.

APPLICATION

Conductors: Install solid conductor for No. 8 AWG and smaller and stranded conductors for No. 6 AWG and larger unless otherwise indicated.

The bonding conductors between the SBB and structural steel of steel-frame buildings shall not be smaller than No. 6 AWG.

The bonding conductors between the PBB and structural steel of steel-frame buildings shall not be smaller than No. 6 AWG.

Underground Grounding Conductors: Install tinned-copper conductor, No. 2 AWG minimum.

Conductor Terminations and Connections:

Pipe and Equipment Grounding Conductor Terminations: Bolted connectors.

Underground Connections: Welded connectors except at test wells and as otherwise indicated.

Connections to Ground Rods at Test Wells: Bolted connectors.

Connections to Structural Steel: Welded connectors.

Conductor Support:

Secure grounding and bonding conductors at intervals of not less than 36 inches

Grounding and Bonding Conductors:

Install in the straightest and shortest route between the origination and termination point, and no longer than required. The bend radius shall not be smaller than eight times the diameter of the conductor. No one bend may exceed 90 degrees.

Install without splices.

Support at not more than 36-inch intervals.

Install grounding and bonding conductors in 3/4-inch PVC conduit until conduit enters a telecommunications room. The grounding and bonding conductor pathway through a plenum shall be in EMT. Conductors shall not be installed in EMT unless otherwise indicated.

If a grounding and bonding conductor is installed in ferrous metallic conduit, bond the conductor to the conduit using a grounding bushing that complies with requirements in Section 27 05 28 "Pathways for Communications Systems," and bond both ends of the conduit to a PBB/SBB.

GROUNDING ELECTRODE SYSTEM

Retain paragraph below if the size of the TBC between the PBB and the ac service is not indicated on Drawings. The length of the TBC should be less than 30 feet (9 m) because the impedance of this conductor, due to its length, limits its effectiveness.

The TBC between the PBB and the ac service equipment ground shall not be smaller than No. 3/0 AWG.

GROUNDING BUSBARS

Indicate locations of grounding busbars on Drawings. Install busbars horizontally, on insulated spacers 2 inches minimum from wall, 12 inches above finished floor unless otherwise indicated.

Where indicated on both sides of doorways, route bus up to top of door frame, across top of doorway, and down; connect to horizontal bus.

CONNECTIONS

Bond metallic equipment in a telecommunications equipment room to the grounding busbar in that room, using equipment grounding conductors not smaller than No. 6 AWG.

Stacking of conductors under a single bolt is not permitted when connecting to busbars.

Assemble the wire connector to the conductor, complying with manufacturer's written instructions and as follows:

Use crimping tool and the die specific to the connector.

Pretwist the conductor.

Apply an antioxidant compound to all bolted and compression connections.

Primary Protector: Bond to the PBB with insulated bonding conductor.

Retain "Interconnections" Paragraph below if all telecommunications backbone and grounding equalizer conductors are not sized on Drawings.

Interconnections: Interconnect all SBBs with the PBB with the telecommunications backbone conductor. If more than one PBB is installed, interconnect PBBs using the grounding equalizer conductor. The telecommunications backbone conductor and grounding equalizer conductor size shall not be less than 2 kcmils/linear foot of conductor length, up to a maximum size of No. 3/0 AWG unless otherwise indicated.

Telecommunications Enclosures and Equipment Racks: Bond metallic components of enclosures to the telecommunications bonding and grounding system. Install [top-mounted] [vertically mounted] rack grounding busbar unless the enclosure and rack are manufactured with the busbar. Bond the equipment grounding busbar to the SBB No. 2 AWG bonding conductors.

Structural Steel: Where the structural steel of a steel frame building is readily accessible within the room or space, bond each SBB and PBB to the vertical steel of the building frame.

Where structural steel is not readily available, provide a ground rod in the telecommunications space or closest communications handhole and bond each respective PBB and/or SBB to the ground rod.

Electrical Power Panelboards: Where an electrical panelboard for telecommunications equipment is located in the same room or space, bond each SBB to the ground bar of the panelboard.

Retain "Shielded Cable" Paragraph below if shielded twisted-pair cables and coaxial cables are installed in communications equipment rooms.

Shielded Cable: Bond the shield of shielded cable to the SBB in communications rooms and spaces. Comply with TIA/EIA-568-B.1 and TIA/EIA-568-B.2 when grounding shielded, balanced, twisted-pair cables.

Rack- and Cabinet-Mounted Equipment: Bond powered equipment chassis to the cabinet or rack grounding bar. Power connection shall comply with CEC; the equipment grounding conductor in the power cord of cord- and plug-connected equipment shall be considered as a supplement to bonding requirements in this Section.

GROUNDING UNDERGROUND DISTRIBUTION SYSTEM COMPONENTS

Retain this article if grounding underground distribution system components is not specified in Section 26 05 26 "Grounding and Bonding for Electrical Systems." Coordinate "Duct-Bank Grounding Conductor" Paragraph below with Drawings and with Section 26 05 43 "Underground Ducts and Raceways for Electrical Systems."

Duct-Bank Grounding Conductor: Bury 12 inches above duct bank when indicated as part of duct-bank installation.

Comply with IEEE C2 grounding requirements.

Grounding Manholes and Handholes: Install a driven ground rod through manhole or handhole floor, close to wall, and set rod depth so 4 inches extends above finished floor. If necessary, install ground rod before manhole is placed and provide No. 1/0 AWG tinned-copper conductor from ground rod into manhole through a waterproof sleeve in manhole wall. Protect ground rods passing through concrete floor with a double wrapping of pressure-sensitive insulating tape or heat-shrunk insulating sleeve from 2 inches above to 6 inches below concrete. Seal floor opening with waterproof, nonshrink grout.

Grounding Connections to Manhole Components: Bond exposed-metal parts such as inserts, cable racks, pulling irons, ladders, and cable shields within each manhole or handhole, to ground rod or grounding conductor. Make connections with No. 4 AWG minimum, bonding conductor. Train conductors level or plumb around corners and fasten to manhole walls. Connect grounding conductors to cable armor and cable shields according to written instructions by manufacturer of splicing and termination kits.

IDENTIFICATION

Labels shall be preprinted or computer-printed type.

Label PBB(s) with "fs-PBB," where "fs" is the telecommunications space identifier for the space containing the PBB.

Label SBB(s) with "fs-SBB," where "fs" is the telecommunications space identifier for the space containing the SBB.

Label the BCT and each telecommunications backbone conductor at its attachment point: "WARNING! TELECOMMUNICATIONS BONDING CONDUCTOR. DO NOT REMOVE OR DISCONNECT!"

FIELD QUALITY CONTROL

Testing Agency: Engage a qualified testing agency to perform tests and inspections.

Tests and Inspections:

Inspect physical and mechanical condition. Verify tightness of accessible, bolted, electrical connections with a calibrated torque wrench according to manufacturer's written instructions.

Test the bonding connections of the system using an ac earth ground-resistance tester, taking two-point bonding measurements in each telecommunications equipment room containing a PBB and a SBB and using the process recommended by BICSI TDMM. Conduct tests with the facility in operation.

Measure the resistance between the busbar and the nearest available grounding electrode. The maximum acceptable value of this bonding resistance is 100 milliohms.

Test for ground loop currents using a digital clamp-on ammeter, with a full-scale of not more than 10 A, displaying current in increments of 0.01 A at an accuracy of plus/minus 2.0 percent.

With the grounding infrastructure completed and the communications system electronics operating, measure the current in every conductor connected to the PBB[ and in each SBB]. Maximum acceptable ac current level is 1 A.

Excessive Ground Resistance: If resistance to ground at the TBC exceeds [5] ohms, notify the District Construction Manager promptly and include recommendations to reduce ground resistance.

See Section 01 40 02 "Quality Requirements / Contractor Laboratory" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

Grounding system will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

END OF SECTION 27 05 26

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021