MasterSpec 2010

SECTION 27 05 44

SLEEVES AND SLEEVE SEALS FOR COMMUNICATIONS PATHWAYS AND CABLING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Sleeves for pathway and cable penetration of non-fire-rated construction walls and floors.

Sleeve-seal systems.

Sleeve-seal fittings.

Grout.

Silicone sealants.

Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 07 84 13 "Penetration Firestopping" for penetration firestopping installed in fire-resistance-rated walls, horizontal assemblies, and smoke barriers, with and without penetrating items.

ACTION SUBMITTALS

Product Data: For each type of product.

PRODUCTS

SLEEVES

Wall Sleeves:

Retain "Steel Pipe Sleeves" or "Cast-Iron Pipe Sleeves" or “PVC Pipe Sleeves” Subparagraph below for penetrations through exterior walls above and below grade.

Steel Pipe Sleeves: ASTM A 53/A 53M, Type E, Grade B, Schedule 40, zinc coated, plain ends.

Cast-Iron Pipe Sleeves: Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop unless otherwise indicated.

PVC Pipe Sleeves:  ASTM 1785, Schedule 40, for below grade only.

Retain "Sleeves for Conduits Penetrating Non-Fire-Rated Gypsum Board Assemblies" Paragraph below for penetrations through non-rated interior partitions.

Sleeves for Conduits Penetrating Non-Fire-Rated Gypsum Board Assemblies: Galvanized-steel sheet; 0.0239-inch minimum thickness; round tube closed with welded longitudinal joint, with tabs for screw-fastening the sleeve to the board.

Sleeves for Rectangular Openings:

Material: Galvanized-steel sheet.

Minimum Metal Thickness:

For sleeve cross-section rectangle perimeter less than 50 inches and with no side larger than 16 inches, thickness shall be 0.052-inch.

For sleeve cross-section rectangle perimeter 50 inches or more and one or more sides larger than 16 inches, thickness shall be 0.138-inch.

GROUT

Description: Nonshrink; recommended for interior and exterior sealing openings in non-fire-rated walls or floors.

Standard: ASTM C 1107/C 1107M, Grade B, post-hardening and volume-adjusting, dry, hydraulic-cement grout.

Design Mix: 5000-psi, 28-day compressive strength.

Packaging: Premixed and factory packaged.

Retain "Silicone Sealants" Article below when use of silicone sealants and silicone foams is permitted as an alternative to grout in sealing of conduit or cable penetrations in gypsum wallboard walls.

SILICONE SEALANTS

Silicone Sealants: Single-component, silicone-based, neutral-curing elastomeric sealants of grade indicated below.

Grade: Pourable (self-leveling) formulation for openings in floors and other horizontal surfaces that are not fire rated.

Sealant shall comply with the testing and product requirements of San Diego Air Pollution Control District Rule 67.0"Architectural Coatings.

Silicone Foams: Multicomponent, silicone-based liquid elastomers that, when mixed, expand and cure in place to produce a flexible, nonshrinking foam.

EXECUTION

SLEEVE INSTALLATION FOR NON-FIRE-RATED ELECTRICAL PENETRATIONS

Comply with NECA 1.

Comply with NEMA VE 2 for cable tray and cable penetrations.

Sleeves for Conduits Penetrating Above-Grade Non-Fire-Rated Concrete and Masonry-Unit Floors and Walls:

Interior Penetrations of Non-Fire-Rated Walls and Floors:

Seal annular space between sleeve and pathway or cable, using joint sealant appropriate for size, depth, and location of joint. Comply with requirements in Section 07 92 00 "Joint Sealants."

Seal space outside of sleeves with mortar or grout. Pack sealing material solidly between sleeve and wall so no voids remain. Tool exposed surfaces smooth; protect material while curing.

Use pipe sleeves unless penetration arrangement requires rectangular sleeved opening.

Size pipe sleeves to provide 1/4-inch annular clear space between sleeve and pathway or cable unless sleeve seal is to be installed.

Install sleeves for wall penetrations unless core-drilled holes or formed openings are used. Install sleeves during erection of walls. Cut sleeves to length for mounting flush with both surfaces of walls. Deburr after cutting.

Retain subparagraph below when unsleeved core-drilled openings in concrete floors are not allowed.

Install sleeves for floor penetrations. Extend sleeves installed in floors 2 inches  above finished floor level. Install sleeves during erection of floors.

Sleeves for Conduits Penetrating Non-Fire-Rated Gypsum Board Assemblies:

Use circular metal sleeves unless penetration arrangement requires rectangular sleeved opening.

Seal space outside of sleeves with approved joint compound for gypsum board assemblies.

Roof-Penetration Sleeves: Seal penetration of individual pathways and cables with flexible boot-type flashing units applied in coordination with roofing work.

Aboveground, Exterior-Wall Penetrations: Seal penetrations using [steel] [cast-iron] pipe sleeves and mechanical sleeve seals. Select sleeve size to allow for 1-inch annular clear space between pipe and sleeve for installing mechanical sleeve seals.

Underground, Exterior-Wall and Floor Penetrations: Install cast-iron pipe sleeves. Size sleeves to allow for 1-inch annular clear space between pathway or cable and sleeve for installing sleeve-seal system.

END OF SECTION 27 05 44

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021