MasterSpec 06/16

SECTION 27 05 53

IDENTIFICATION FOR COMMUNICATIONS SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Color and legend requirements for labels and signs.

Labels.

Bands and tubes.

Tapes.

Signs.

Cable ties.

Fasteners for labels and signs.

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for communications identification products.

Retain "Samples" Paragraph below for single-stage Samples if Project requirements are complex.

Samples: For each type of label and sign to illustrate composition, size, colors, lettering style, mounting provisions, and graphic features of identification products.

Identification Schedule:

Outlets: Scaled drawings indicating location and proposed designation.

Backbone Cabling: Riser diagram showing each communications room, backbone cable, and proposed backbone cable designation.

Racks: Scaled drawings indicating location and proposed designation.

Patch Panels: Enlarged scaled drawings showing rack row, number, and proposed designations.

PRODUCTS

PERFORMANCE REQUIREMENTS

Comply with CEC and TIA 606-B.

Comply with ANSI Z535.4 for safety signs and labels.

Retain first paragraph below if retaining self-adhesive products.

Adhesive-attached labeling materials, including label stocks, laminating adhesives, and inks used by label printers, shall comply with UL 969.

Thermal Movements: Allow for thermal movements from ambient and surface temperature changes.

Temperature Change:  120 deg F, ambient; 180 deg F, material surfaces.

COLOR AND LEGEND REQUIREMENTS

Equipment Identification Labels:

Black letters on a white field.

Coordinate retained Section Text articles with "Installation" and "Identification Schedule" articles.

LABELS

Vinyl Wraparound Labels: Preprinted, flexible labels laminated with a clear, weather- and chemical-resistant coating and matching wraparound clear adhesive tape for securing label ends.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Grafoplast Wire Markers.

Ideal Industries, Inc.

Or equal.

Snap-Around Labels: Slit, pretensioned, flexible, preprinted, color-coded acrylic sleeves, with diameters sized to suit diameters of raceway or cable they identify, that stay in place by gripping action.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Grafoplast Wire Markers.

Ideal Industries, Inc.

Or equal.

Self-Adhesive Wraparound Labels: [Preprinted] [Write-on], 3-mil-thick, [polyester] [vinyl] flexible labels with acrylic pressure-sensitive adhesive.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Grafoplast Wire Markers.

Ideal Industries, Inc.

Or equal.

Self-Lamination: Clear; UV-, weather- and chemical-resistant; self-laminating protective shields over the legend. Labels sized such that the clear shield overlaps the entire printed legend.

Retain one of two "Marker for Labels" subparagraphs below.

Marker for Labels: Permanent, waterproof black ink marker recommended by tag manufacturer.

Marker for Labels: Machine-printed, permanent, waterproof black ink recommended by printer manufacturer.

Self-Adhesive Labels: [Polyester] [Vinyl], thermal, transfer-printed, 3-mil-thick, multicolor, weather- and UV-resistant, pressure-sensitive adhesive labels, configured for intended use and location.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Grafoplast Wire Markers.

Ideal Industries, Inc.

Or equal.

Minimum Nominal Size:

1-1/2 by 6 inches for raceway and conductors.

3-1/2 by 5 inches for equipment.

As required by authorities having jurisdiction.

BANDS AND TUBES

Snap-Around, Color-Coding Bands: Slit, pretensioned, flexible, solid-colored acrylic sleeves, 2 inches long, with diameters sized to suit diameters of raceway or cable they identify, that stay in place by gripping action.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Grafoplast Wire Markers.

Ideal Industries, Inc.

Or equal.

UNDERGROUND-LINE WARNING TAPE

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Brady Corporation.

Grafoplast Wire Markers.

Ideal Industries, Inc.

Or equal.

Tape:

Recommended by manufacturer for the method of installation and suitable to identify and locate underground communications utility lines.

Printing on tape shall be permanent and shall not be damaged by burial operations.

Tape material and ink shall be chemically inert and not subject to degradation when exposed to acids, alkalis, and other destructive substances commonly found in soils.

Color and Printing:

Comply with ANSI Z535.1, ANSI Z535.2, ANSI Z535.3, and ANSI Z535.4.

Inscriptions for Orange-Colored Tapes: "TELEPHONE CABLE, CATV CABLE, COMMUNICATIONS CABLE, OPTICAL-FIBER CABLE".

Tag: [Type ID]:

Detectable three-layer laminate, consisting of a printed pigmented polyolefin film, a solid aluminum-foil core, and a clear protective film that allows inspection of the continuity of the conductive core; bright colored, [continuous-printed on one side with the inscription of the utility, ]compounded for direct-burial service.

Width: 3 inches.

Overall Thickness: 5 mils.

Foil Core Thickness: 0.35 mil.

Weight: 28 lb/1000 sq. ft..

Tensile according to ASTM D 882: 70 lbf and 4600 psi.

SIGNS

Baked-Enamel Signs:

Manufacturers: Subject to compliance with requirements, provide products by the following:

Carlton Industries, LP.

Or equal.

Preprinted aluminum signs, [high-intensity reflective] punched or drilled for fasteners, with colors, legend, and size required for application.

1/4-inch grommets in corners for mounting.

Nominal Size: 7 by 10 inches.

Metal-Backed Butyrate Signs:

Manufacturers: Subject to compliance with requirements, provide products by the following:

Carlton Industries, LP.

Or equal.

Weather-resistant, nonfading, preprinted, cellulose-acetate butyrate signs, with 0.0396-inch galvanized-steel backing, punched and drilled for fasteners, and with colors, legend, and size required for application.

1/4-inch grommets in corners for mounting.

Nominal Size: 10 by 14 inches.

Laminated-Acrylic or Melamine-Plastic Signs:

Manufacturers: Subject to compliance with requirements, provide products by the following:

Carlton Industries, LP.

Or equal.

Engraved legend.

Thickness:

For signs up to 20 sq. in., minimum 1/16 inch thick.

For signs larger than 20 sq. in., 1/8 inch thick.

Retain first option in first subparagraph below for instruction signs; retain second option for identification signs.

Engraved legend with [black letters on white face] [white letters on a dark gray background].

[Punched or drilled for mechanical fasteners with 1/4-inch grommets in corners for mounting] [Self-adhesive].

Framed with mitered acrylic molding and arranged for attachment at applicable equipment.

CABLE TIES

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

HellermannTyton.

Or equal.

Retain one or more of "General-Purpose Cable Ties," "UV-Stabilized Cable Ties," and "Plenum-Rated Cable Ties" paragraphs below. Coordinate with "Installation" Article.

General-Purpose Cable Ties: Fungus inert, self-extinguishing, one piece, self-locking, and Type 6/6 nylon.

Minimum Width: 3/16 inch.

Tensile Strength at 73 deg F according to ASTM D 638: 12,000 psi.

Temperature Range: Minus 40 to plus 185 deg F.

Color: Black, except where used for color-coding.

UV-Stabilized Cable Ties: Fungus inert, designed for continuous exposure to exterior sunlight, self-extinguishing, one piece, self-locking, and Type 6/6 nylon.

Minimum Width: 3/16 inch.

Tensile Strength at 73 deg F according to ASTM D 638: 12,000 psi.

Temperature Range: Minus 40 to plus 185 deg F.

Color: Black.

Plenum-Rated Cable Ties: Self-extinguishing, UV stabilized, one piece, and self-locking.

Minimum Width: 3/16 inch.

Tensile Strength at 73 deg F according to ASTM D 638: 7000 psi.

UL 94 Flame Rating: 94V-0.

Temperature Range: Minus 50 to plus 284 deg F.

Color: Black.

MISCELLANEOUS IDENTIFICATION PRODUCTS

Paint: Comply with requirements in painting Sections for paint materials and application requirements. Retain paint system applicable for surface material and location (exterior or interior).

Fasteners for Labels and Signs: Self-tapping, stainless-steel screws or stainless-steel machine screws with nuts and flat and lock washers.

EXECUTION

PREPARATION

Self-Adhesive Identification Products: Before applying communications identification products, clean substrates of substances that could impair bond, using materials and methods recommended by manufacturer of identification product.

INSTALLATION

Verify and coordinate identification names, abbreviations, colors, and other features with requirements in other Sections requiring identification applications, Drawings, Shop Drawings, manufacturer's wiring diagrams, and operation and maintenance manual. Use consistent designations throughout Project.

Install identifying devices before installing acoustical ceilings and similar concealment.

Verify identity of each item before installing identification products.

Coordinate identification with Project Drawings, manufacturer's wiring diagrams, and operation and maintenance manual.

Apply identification devices to surfaces that require finish after completing finish work.

Install signs with approved legend to facilitate proper identification, operation, and maintenance of communications systems and connected items.

Elevated Components: Increase sizes of labels, signs, and letters to those appropriate for viewing from the floor.

Vinyl Wraparound Labels:

Secure tight to surface of raceway or cable at a location with high visibility and accessibility.

Attach labels that are not self-adhesive type with clear vinyl tape, with adhesive appropriate to the location and substrate.

Provide label 6 inches from cable end.

Snap-Around Labels:

Secure tight to surface at a location with high visibility and accessibility.

Provide label 6 inches from cable end.

Self-Adhesive Wraparound Labels:

Secure tight to surface at a location with high visibility and accessibility.

Provide label 6 inches from cable end.

Self-Adhesive Labels:

On each item, install unique designation label that is consistent with wiring diagrams, schedules, and operation and maintenance manual.

Unless otherwise indicated, provide a single line of text with 1/2-inch-high letters on 1-1/2-inch-high label; where two lines of text are required, use labels 2 inches high.

Snap-Around, Color-Coding Bands: Secure tight to surface at a location with high visibility and accessibility.

Underground-Line Warning Tape:

During backfilling of trenches, install continuous underground-line warning tape directly above cable or raceway at 6 to 8 inches below finished grade. Use multiple tapes where width of multiple lines installed in a common trench [or concrete envelope] exceeds 16 inches overall.

Install underground-line warning tape for direct-buried cables and cables in raceways.

Cable Ties: General purpose, except as listed below:

Outdoors: UV-stabilized nylon.

In Spaces Handling Environmental Air: Plenum rated.

IDENTIFICATION SCHEDULE

Install identification materials and devices at locations for most convenient viewing without interference with operation and maintenance of equipment. Install access doors or panels to provide view of identifying devices.

Identify conductors, cables, and terminals in enclosures and at junctions, terminals, pull points, and locations with high visibility. Identify by system and circuit designation.

Accessible Fittings for Raceways and Cables within Buildings: Identify covers of each junction and pull box with self-adhesive labels containing wiring system legend.

System legends shall be as follows:

Telecommunications.

Faceplates: Label individual faceplates with self-adhesive labels. Place label at top of faceplate. Each faceplate shall be labeled with its individual, sequential designation[, numbered clockwise when entering room from primary egress], composed of the following, in the order listed:

Wiring closet designation.

Colon.

Faceplate number.

Equipment Room Labeling:

Racks, Frames, and Enclosures: Identify front and rear of each with self-adhesive labels[ containing equipment designation].

Patch Panels: [Label individual rows in each rack, starting at top and working down, with self-adhesive labels.] [Label individual rows and outlets, starting at to left and working down, with self-adhesive labels.]

Data Outlets: Label each outlet with a self-adhesive label indicating the following, in the order listed:

Room number being served.

Colon.

Faceplate number.

Backbone Cables: Label each cable with a [vinyl-wraparound label] [snap-around label] [self-adhesive wraparound label] indicating the location of the far or other end of the backbone cable. Patch panel or punch down block where cable is terminated should be labeled identically.

Horizontal Cables: Label each cable with a [vinyl-wraparound label] [snap-around label] [self-adhesive wraparound label] indicating the following, in the order listed:

Room number.

Colon.

Faceplate number.

Locations of Underground Lines: Underground-line warning tape for copper, coaxial, hybrid copper/fiber, and optical-fiber cable.

Instructional Signs: Self-adhesive labels.

Warning Labels for Indoor Cabinets, Boxes, and Enclosures: [Self-adhesive labels] [Baked-enamel warning signs] [Metal-backed, butyrate warning signs].

Apply to exterior of door, cover, or other access.

Coordinate "Equipment Identification Labels" Paragraph below with communications Sections. Delete items not in Project.

Equipment Identification Labels:

Indoor Equipment: [Self-adhesive label] [Baked-enamel signs] [Metal-backed butyrate signs] [Laminated-acrylic or melamine-plastic sign].

Outdoor Equipment: [Laminated-acrylic or melamine-plastic sign] [Stenciled legend 4 inches high].

Equipment to Be Labeled:

Communications cabinets.

Uninterruptible power supplies.

Computer room air conditioners.

Fire-alarm and suppression equipment.

Egress points.

Power distribution components.

END OF SECTION 27 05 53

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021