MasterSpec 06/16

SECTION 27 11 00

COMMUNICATIONS EQUIPMENT ROOM FITTINGS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Backboards.

Boxes, enclosures, and cabinets.

Power strips.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 27 13 13 "Communications Copper Backbone Cabling" for copper data cabling associated with system panels and devices.

Section 27 13 23 "Communications Optical Fiber Backbone Cabling" for optical-fiber data cabling associated with system panels and devices.

Section 27 13 33 "Communications Coaxial Backbone Cabling" for coaxial data cabling associated with system panels and devices.

Section 27 15 13 "Communications Copper Horizontal Cabling" for copper data cabling associated with system panels and devices.

Section 27 15 23 "Communications Optical Fiber Horizontal Cabling" for coaxial data cabling associated with system panels and devices.

Section 27 15 33 "Communications Coaxial Horizontal Cabling" for coaxial data cabling associated with system panels and devices.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Definitions of "access provider" and "service provider" are derived from BICSI's "Telecommunications Distribution Methods Manual."

Access Provider: An operator that provides a circuit path or facility between the service provider and user. An access provider can also be a service provider.

RCDD: Registered communications distribution designer.

Service Provider: The operator of a telecommunications transmission service delivered through access provider facilities.

PBB: Primary bonding bus bar.

SBB: secondary bonding bus bar.

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for equipment racks and cabinets.

Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Shop Drawings: For communications equipment room fittings. Include plans, elevations, sections, details, and attachments to other work.

Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Equipment Racks and Cabinets: Include workspace requirements and access for cable connections.

Grounding: Indicate location of grounding bus bar and its mounting detail showing standoff insulators and wall mounting brackets.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Series 01 40 ## "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For Installer, qualified layout technician, installation supervisor, and field inspector.

QUALITY ASSURANCE

Installer Qualifications: Cabling installer must have personnel certified by BICSI on staff.

Layout Responsibility: Preparation of Shop Drawings shall be under direct supervision of [RCDD] [Technician].

Installation Supervision: Installation shall be under direct supervision of [Technician] [Installer 2, Copper or Fiber], who shall be present at all times when Work of this Section is performed at Project site.

Field Inspector: Currently registered by BICSI as [RCDD] [Technician] to perform the on-site inspection.

PRODUCTS

BACKBOARDS

Backboards: Plywood, fire-retardant treated,  3/4 by 48 by 96 inches.

Backboard Paint:  Light-colored fire-retardant paint.

For 19-inch- and 23-inch-wide racks, frames, and enclosures, see Section 27 11 16 "Communications Racks, Frames, and Enclosures."

BOXES, ENCLOSURES, AND CABINETS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Hoffman; a brand of Pentair Equipment Protection.

Hubbell Incorporated.

RACO; Hubbell.

Or equal.

General Requirements for Boxes, Enclosures, and Cabinets: Boxes, enclosures, and cabinets shall be listed and labeled for intended location and use.

Sheet Metal Outlet and Device Boxes: Comply with NEMA OS 1 and UL 514A.

Cast-Metal Outlet and Device Boxes: Comply with NEMA FB 1, Type FD, ferrous alloy, with gasketed cover.

Nonmetallic Outlet and Device Boxes: Comply with NEMA OS 2 and UL 514C.

Small Sheet Metal Pull and Junction Boxes: NEMA OS 1.

Cast-Metal Access, Pull, and Junction Boxes: Comply with NEMA FB 1 and UL 1773, galvanized cast iron with gasketed cover.

Box extensions used to accommodate new building finishes shall be of same material as recessed box.

Device Box Dimensions:  4 inches square by 2-1/8 inches deep.

Coordinate "Hinged-Cover Enclosures" Paragraph below with Drawings, if hinged-cover enclosures other than NEMA 250, Type 1 are required, such as for very dusty areas, or if consideration should be given to use of NEMA 250, Type 3R or Type 12 enclosures.

Hinged-Cover Enclosures: Comply with UL 50 and NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 12] with continuous-hinge cover with flush latch unless otherwise indicated.

Metal Enclosures: Steel, finished inside and out with manufacturer's standard enamel.

Nonmetallic Enclosures: [Plastic] [Fiberglass].

Interior Panels: Steel; all sides finished with manufacturer's standard enamel.

Cabinets:

NEMA 250, [Type 1] [Type 3R] [Type 12] galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

Hinged door in front cover with flush latch and concealed hinge.

Key latch to match panelboards.

Metal barriers to separate wiring of different systems and voltage.

Accessory feet where required for freestanding equipment.

Nonmetallic cabinets shall be listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

POWER STRIPS

Comply with requirements in Section 27 11 16 "Communications Racks, Frames, and Enclosures."

EXECUTION

ENTRANCE FACILITIES

Retain first paragraph below if demarcation point and service entrance cabling are from telecommunications service provider.

Contact telecommunications service provider and arrange for installation of demarcation point, protected entrance terminals, and a housing when so directed by service provider.

Comply with requirements in Section 27 05 28 "Pathways for Communications Systems" for materials and installation requirements for [underground] [buried] [aerial] pathways.

INSTALLATION

Comply with NECA 1.

Comply with BICSI's "Telecommunications Distribution Methods Manual" for layout of communications equipment spaces.

Comply with BICSI's "Information Technology Systems Installation Methods Manual" for installation of equipment in communications equipment spaces.

Bundle, lace, and train conductors and cables to terminal points without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

Revise paragraphs below to specify coordination with other parties involved in finalizing communications equipment room Work.

Coordinate layout and installation of communications equipment in tracks and in room. Coordinate service entrance configuration with service provider.

Meet jointly with systems providers, equipment suppliers, and Owner to exchange information and agree on details of equipment configurations and installation interfaces.

Record agreements reached in meetings and distribute them to other participants.

Adjust configurations and locations of distribution frames, cross-connects, and patch panels in equipment rooms to accommodate and optimize configurations and space requirements of communications equipment.

Adjust configurations and locations of equipment with distribution frames, cross-connects, and patch panels of cabling systems of other communications, electronic safety and security, and related systems that share space in equipment room.

Coordinate location of power raceways and receptacles with locations of communications equipment requiring electrical power to operate.

Backboards:

Install from 8 inches to 8 feet, 6 inches above finished floor. If plywood is fire rated, ensure that fire-rating stamp is visible after installation.

Paint all sides of backboard with two coats of paint, leaving fire rating stamp visible.

Comply with requirements for backboard installation in BICSI's "Information Technology Systems Installation Methods Manual" and TIA-569-D.

SLEEVE AND SLEEVE SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 27 05 44 "Sleeves and Sleeve Seals for Communications Pathways and Cabling."

FIRESTOPPING

Comply with requirements in Section 07 84 13 "Penetration Firestopping."

Comply with TIA-569-D, Annex A, "Firestopping."

Comply with BICSI's "Information Technology Systems Installation Methods Manual," "Firestopping Practices" Ch.

END OF SECTION 27 11 00

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021