MasterSpec 06/16

SECTION 27 13 13

COMMUNICATIONS COPPER BACKBONE CABLING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

High-count Category 5e twisted pair cable.

Twisted pair cable hardware, including plugs, jacks, patch panels, and cross-connects.

Grounding provisions for twisted pair cable.

Cabling identification.

Source quality control requirements for twisted pair cable.

Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 27 13 23 "Communications Optical Fiber Backbone Cabling" for optical fiber data cabling associated with system panels and devices.

Section 27 13 33 "Communications Coaxial Backbone Cabling" for coaxial fiber data cabling associated with system panels and devices

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.  Add terms that are not specified in 01 42 00 “References”.

Cross-Connect: A facility enabling the termination of cable elements and their interconnection or cross-connection.

EMI: Electromagnetic interference.

F/FTP: Overall foil screened cable with foil screened twisted pair.

FTP: Shielded twisted pair.

F/UTP: Overall foil screened cable with unscreened twisted pair.

IDC: Insulation displacement connector.

Jack: Also commonly called an "outlet," it is the fixed, female connector.

LAN: Local area network.

Plug: Also commonly called a "connector," it is the removable, male telecommunications connector.

RCDD: Registered Communications Distribution Designer.

Screen: A metallic layer, either a foil or braid, placed around a pair or group of conductors.

S/FTP: Overall braid screened cable with foil screened twisted pair.

Shield: A metallic layer, either a foil or braid, placed around a pair or group of conductors.

S/UTP: Overall braid screened cable with unscreened twisted pairs.

UTP: Unscreened (unshielded) twisted pair.

COPPER BACKBONE CABLING DESCRIPTION

Copper backbone cabling system shall provide interconnections between communications equipment rooms, main terminal space, and entrance facilities in the telecommunications cabling system structure. Cabling system consists of backbone cables, intermediate and main cross-connects, mechanical terminations, and patch cords or jumpers used for backbone-to-backbone cross-connection.

Backbone cabling cross-connects may be located in communications equipment rooms or at entrance facilities. Bridged taps and splitters shall not be used as part of backbone cabling.

ACTION SUBMITTALS

Product Data: For each type of product.

Shop Drawings: Reviewed and stamped by RCDD.

Revise paragraphs below to reflect District's requirements. Retain one of two "System Labeling Schedules" subparagraphs below.

System Labeling Schedules: Electronic copy of labeling schedules, in software and format selected by District.

System Labeling Schedules: Electronic copy of labeling schedules that are part of the cabling and asset identification system of the software.

Cabling administration Drawings and printouts.

Wiring diagrams to show typical wiring schematics, including the following:

Telecommunications rooms plans and elevations.

Telecommunications pathways.

Telecommunications system access points.

Telecommunications grounding system

Cross-connects.

Patch panels.

Patch cords.

Cross-Connects and Patch Panels: Detail mounting assemblies, and show elevations and physical relationship between the installed components.

Twisted pair cable testing plan.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For [RCDD, ] [Installer, ] installation supervisor, and field inspector.

Source quality-control reports.

Retain "Product Certificates" Paragraph below to require submittal of product certificates from manufacturers.

Product Certificates: For each type of product.

Field quality-control reports.

CLOSEOUT SUBMITTALS

Maintenance Data: For splices and connectors to include in maintenance manuals.

QUALITY ASSURANCE

Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

Layout Responsibility: Preparation of Shop Drawings[ and cabling administration Drawings][, cabling administration Drawings, and field testing program development] by [an RCDD] [a Technician].

Installation Supervision: Installation shall be under the direct supervision of [Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

DELIVERY, STORAGE, AND HANDLING

According to BICSI's ITSIMM cables should be tested upon receipt.

Test cables upon receipt at Project site.

Test each pair of twisted pair cable for open and short circuits.

PROJECT CONDITIONS

Environmental Limitations: Do not deliver or install cables and connecting materials until wet work in spaces is complete and dry, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

COORDINATION

Revise this article to specify coordination with other parties involved in finalizing communications equipment room work.

Coordinate layout and installation of telecommunications pathways and cabling with District’s telecommunications and LAN equipment and service suppliers.

PRODUCTS

PERFORMANCE REQUIREMENTS

General Performance: Backbone cabling system shall comply with transmission standards in TIA-568-C.1, when tested according to test procedures of this standard.

Surface-Burning Characteristics: As determined by testing identical products according to ASTM E 84 by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

Flame-Spread Index: [25] or less.

Smoke-Developed Index: [50] [450] or less.

Telecommunications Pathways and Spaces: Comply with TIA-569-D.

Grounding: Comply with TIA-607-B.

GENERAL CABLE CHARACTERISTICS

Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with the applicable standard and CEC for the following types:

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project. Retain options if "permitted substitutions," as defined in CEC, are appropriate for this Project. Note that plenum-rated cable may be substituted for riser cable; however, riser cable may not be substituted for plenum cable.

Communications, Plenum Rated: Type CMP complying with UL 1685[ or Type CMP in listed plenum communications raceway] [ or Type CMP in listed cable routing assembly].

Communications, Riser Rated: Type CMP or Type CMR in listed plenum or riser communications raceway.

Surface-Burning Characteristics: Comply with ASTM E 84; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

Flame-Spread Index: [25] or less.

Smoke-Developed Index: [50] [450] or less.

RoHS compliant.

HIGH-COUNT CATEGORY 5e TWISTED PAIR CABLE

Description: [25] [50]-pair, balanced-twisted pair cable, certified to meet transmission characteristics of Category 5e cable at frequencies up to 100 MHz.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Belden Inc.

Berk-Tek Leviton; a Nexans/Leviton alliance.

CommScope, Inc.

Or equal.

Standard: Comply with ICEA S-90-661, NEMA WC 63.1, and TIA-568-C.2 for Category 5e cables.

Conductors: 100-ohm, 24 AWG solid copper.

Shielding/Screening:  Unshielded balanced twisted pairs (UTP).

Cable Rating: [Indoor/Outdoor] [Riser] [Plenum].

Jacket: Black thermoplastic.

TWISTED PAIR CABLE HARDWARE

Description: Hardware designed to connect, splice, and terminate twisted pair copper communications cable.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Belden CDT Networking Division/NORDX.

Berk-Tek Leviton; a Nexans/Leviton alliance.

CommScope, Inc.

Or equal.

Retain "General Requirements for Cable Connecting Hardware" Paragraph below to specify performance requirements for all twisted pair hardware specified in this article.

General Requirements for Cable Connecting Hardware:

Twisted pair cable hardware shall meet the performance requirements of Category 5e.

Comply with TIA-568-C.2, IDC type, with modules designed for punch-down caps or tools.

Cables shall be terminated with connecting hardware of same category or higher.

Source Limitations:  Obtain twisted pair cable hardware from single source from single manufacturer.

Patch Panel: Modular panels housing numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.

Features:

Universal T568A and T568B wiring labels.

Labeling areas adjacent to conductors.

24 or 48 ports.

Construction: 16-gauge steel and mountable on 19-inch equipment racks.

Number of Jacks per Field: One for each four-pair conductor group of indicated cables, plus spares and blank positions adequate to suit specified expansion criteria.

Jacks and Jack Assemblies:

Female; eight position; modular; fixed telecommunications connector designed for termination of a single four-pair 100-ohm unshielded or shielded twisted pair cable.

Designed to snap-in to a patch panel or faceplate.

Standard: Comply with TIA-568-C.2.

Cords are generally available in lengths of up to 20 feet (6 m) and longer in 24-inch (600-mm) increments.

Patch Cords: Factory-made, four-pair cables in [36-inch] [48-inch] lengths; terminated with an eight-position modular plug at each end.

Patch cords shall have color-coded boots for circuit identification.

CABLING IDENTIFICATION

Comply with TIA-606-B and UL 969 for a system of labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

GROUNDING

Comply with requirements in Section 27 05 26 "Grounding and Bonding for Communications Systems" for grounding conductors and connectors.

Comply with TIA-607-C.

SOURCE QUALITY CONTROL

Factory test cables on reels according to TIA-568-C.1.

Factory test cables according to TIA-568-C.2.

See Series 01 40 ## "Quality Requirements" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

Cable will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

EXECUTION

ENTRANCE FACILITIES

Retain this article if service entrance cabling and demarcation point are provided by communications service provider.

Coordinate backbone cabling with the protectors and demarcation point provided by communications service provider.

WIRING METHODS

Retain one of two "Wiring Method" paragraphs below and coordinate with Drawings. Delete both if wiring methods for system are indicated on Drawings.

Wiring Method: Install cables in raceways and cable trays, except within consoles, cabinets, desks, and counters and except in accessible ceiling spaces, attics, and gypsum board partitions where unenclosed wiring method may be used. Conceal raceway and cables, except in unfinished spaces.

Install plenum cable in environmental air spaces, including plenum ceilings.

Comply with requirements for raceways and boxes specified in Section 27 05 28 "Pathways for Communications Systems."

Wiring within Enclosures: Bundle, lace, and train cables within enclosures. Connect to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools. Install cables parallel with or at right angles to sides and back of enclosure.

INSTALLATION OF PATHWAYS

Coordinate cable-connection hardware installations and specialty arrangements with layout Drawings and with requirements specified for communications equipment rooms. If Drawings are explicit enough, these requirements may be reduced or omitted.

Comply with requirements for demarcation point, cabinets, and racks specified in Section 27 11 00 "Communications Equipment Room Fittings."

Comply with Section 27 05 28 "Pathways for Communications Systems."

Comply with Section 27 05 29 "Hangers and Supports for Communications Systems."

Drawings indicate general arrangement of pathways and fittings.

INSTALLATION OF COPPER BACKBONE CABLES

Comply with NECA 1 and NECA/BICSI 568.

General Requirements for Cabling:

Comply with TIA-568-C.0, TIA-568-C.1, and TIA-568-C.2.

Comply with BICSI's "Information Transport Systems Installation Methods Manual (ITSIMM)," Ch. 5, "Copper Structured Cabling Systems," "Cable Termination Practices" Section.

Install 110-style IDC termination hardware unless otherwise indicated.

Do not untwist twisted pair cables more than 1/2 inch from the point of termination to maintain cable geometry.

Terminate all conductors; no cable shall contain unterminated elements. Make terminations only at indicated outlets, terminals, cross-connects, and patch panels.

Cables may not be spliced. Secure and support cables at intervals not exceeding 30 inches and not more than 6 inches from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

Install lacing bars to restrain cables, prevent straining connections, and prevent bending cables to smaller radii than minimums recommended by manufacturer.

Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIMM, Ch. 5, "Copper Structured Cabling Systems," "Cable Termination Practices" Section Use lacing bars and distribution spools.

Do not install bruised, kinked, scored, deformed, or abraded cable. Do not splice cable between termination, tap, or junction points. Remove and discard cable if damaged during installation, and replace it with new cable.

Cold-Weather Installation: Bring cable to room temperature before dereeling. Heat lamps shall not be used for heating.

In the communications equipment room, install a 10-foot-long service loop on each end of cable.

Pulling Cable: Comply with BICSI ITSIMM, Ch. 5, "Copper Structured Cabling Systems," "Pulling and Installing Cable" Section. Monitor cable pull tensions.

Open-Cable Installation:

Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

Suspend twisted pair cabling, not in a wireway or pathway, a minimum of 8 inches above ceilings by cable supports not more than [60 inches] apart.

Cable shall not be run through structural members or in contact with pipes, ducts, or other potentially damaging items.

Installation of Cable Routed Exposed under Raised Floors:

Install plenum-rated cable only.

Install cabling after the flooring system has been installed in raised floor areas.

Coil cable [6 feet] long not less than [12 inches] in diameter below each feed point.

Group connecting hardware for cables into separate logical fields.

Separation from EMI Sources:

Comply with recommendations from BICSI's "Telecommunications Distribution Methods Manual" and TIA-569-D for separating unshielded copper communication cable from potential EMI sources, including electrical power lines and equipment.

Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

Electrical Equipment Rating Less Than 2 kVA: A minimum of 5 inches.

Electrical Equipment Rating between 2 and 5 kVA: A minimum of 12 inches.

Electrical Equipment Rating More Than 5 kVA: A minimum of 24 inches.

Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

Electrical Equipment Rating Less Than 2 kVA: A minimum of 2-1/2 inches.

Electrical Equipment Rating between 2 and 5 kVA: A minimum of 6 inches.

Electrical Equipment Rating More Than 5 kVA: A minimum of 12 inches.

Separation between communications cables in grounded metallic raceways, power lines, and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

Electrical Equipment Rating Less Than 2 kVA: No requirement.

Electrical Equipment Rating between 2 and 5 kVA: A minimum of 3 inches.

Electrical Equipment Rating More Than 5 kVA: A minimum of 6 inches.

Separation between Communications Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger: A minimum of 48 inches.

Separation between Communications Cables and Fluorescent Fixtures: A minimum of 5 inches.

FIRESTOPPING

Comply with requirements in Section 07 84 13 "Penetration Firestopping."

Comply with TIA-569-D, Annex A, "Firestopping."

Comply with "Firestopping Systems" Article in BISCI's "Telecommunications Distribution Methods Manual."

GROUNDING

Install grounding according to the "Grounding, Bonding, and Electrical Protection" chapter in BICSI's "Telecommunications Distribution Methods Manual."

Comply with TIA-607-C and NECA/BICSI-607.

Locate grounding bus bar to minimize the length of bonding conductors. Fasten to wall, allowing at least a 2-inch clearance behind the grounding bus bar. Connect grounding bus bar to suitable electrical building ground, using a minimum No. 4 AWG grounding electrode conductor.

Bond metallic equipment to the grounding bus bar, using not smaller than a No. 6 AWG equipment grounding conductor.

IDENTIFICATION

Identify system components, wiring, and cabling complying with TIA-606-B. Comply with requirements for identification specified in Section 27 05 53 "Identification for Communications Systems."

Administration Class:  3.

Color-code cross-connect fields and apply colors to voice and data service backboards, connections, covers, and labels.

Paint and label colors for equipment identification shall comply with TIA-606-B for Class 3 level of administration, including optional identification requirements of this standard.

Comply with requirements in Section 27 15 13 "Communications Copper Horizontal Cabling" for cable and asset management software.

Cable Schedule: Install in a prominent location in each equipment room and wiring closet. List incoming and outgoing cables and their designations, origins, and destinations. Protect with rigid frame and clear plastic cover. Furnish an electronic copy of final comprehensive schedules for Project.

Cabling Administration Drawings: Show building floor plans with cabling administration-point labeling. Identify labeling convention and show labels for telecommunications closets, backbone pathways and cables, entrance pathways and cables, terminal hardware and positions, horizontal cables, work areas and workstation terminal positions, grounding buses and pathways, and equipment grounding conductors.

Cable and Wire Identification:

Label each cable within 4 inches of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

Each wire connected to building-mounted devices is not required to be numbered at the device if wire color is consistent with associated wire connected and numbered within panel or cabinet.

Exposed Cables and Cables in Cable Trays and Wire Troughs: Label each cable at intervals not exceeding 15 feet.

Label each terminal strip, and screw terminal in each cabinet, rack, or panel.

Individually number wiring conductors connected to terminal strips, and identify each cable or wiring group, extended from a panel or cabinet to a building-mounted device, with the name and number of a particular device.

Label each unit and field within distribution racks and frames.

Identification within Connector Fields in Equipment Rooms and Wiring Closets: Label each connector and each discrete unit of cable-terminating and -connecting hardware. Where similar jacks and plugs are used for both voice and data communication cabling, use a different color for jacks and plugs of each service.

Labels shall be preprinted or computer-printed type, with a printing area and font color that contrast with cable jacket color but still comply with TIA-606-B requirements for the following:

Cables use flexible vinyl or polyester that flexes as cables are bent.

FIELD QUALITY CONTROL

Perform tests and inspections.

Retain "Tests and Inspections" Paragraph below to describe tests and inspections to be performed.

Tests and Inspections:

Visually inspect jacket materials for NRTL certification markings. Inspect cabling terminations in communications equipment rooms for compliance with color-coding for pin assignments, and inspect cabling connections for compliance with TIA-568-C.1.

Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

Test cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors. Test operation of shorting bars in connection blocks. Test cables after termination but not cross-connection.

Test instruments shall meet or exceed applicable requirements in TIA-568-C.2. Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex. Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

Data for each measurement shall be documented. Data for submittals shall be printed in a summary report that is formatted similarly to Table 10.1 in BICSI's "Telecommunications Distribution Methods Manual," or shall be transferred from the instrument to the computer, saved as text files, printed, and submitted.

Remove and replace cabling where test results indicate that they do not comply with specified requirements.

See Series 01 40 ## "Quality Requirements" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

End-to-end cabling will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

END OF SECTION 27 13 13

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021