MasterSpec 06/16

SECTION 27 15 23

COMMUNICATIONS OPTICAL FIBER HORIZONTAL CABLING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

850 nanometer laser-optimized 50/125 micrometer multimode optical fiber cable (OM4).

Optical fiber cable connecting hardware, patch panels, and cross-connects.

Grounding.

Cabling identification products.

Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 27 15 13 "Communications Copper Horizontal Cabling" for copper data cabling associated with system panels and devices.

Section 27 15 33 "Communications Coaxial Horizontal Cabling" for coaxial data cabling associated with system panels and devices

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.  Add terms that are not specified in 01 42 00 “References”.

Cross-Connect: A facility enabling the termination of cable elements and their interconnection or cross-connection.

RCDD: BICSI Registered Communications Distribution Designer.

OPTICAL FIBER HORIZONTAL CABLING DESCRIPTION

Optical fiber horizontal cabling system shall provide interconnections between Distributor A, Distributor B, or Distributor C and the equipment outlet, otherwise known as "Cabling Subsystem 1" in the telecommunications cabling system structure. Cabling system consists of horizontal cables, intermediate and main cross-connects, mechanical terminations, and patch cords or jumpers used for horizontal-to-horizontal cross-connection.

TIA-568-C.1 requires that a minimum of two equipment outlets be installed for each work area.

Horizontal cabling shall contain no more than one transition point or consolidation point between the horizontal cross-connect and the equipment outlet.

Bridged taps and splices shall not be installed in the horizontal cabling.

A work area is approximately 100 sq. ft., and includes the components that extend from the equipment outlets to the equipment.

The maximum allowable horizontal cable length is 295 feet. This maximum allowable length does not include an allowance for the length of 16 feet to the workstation equipment or in the horizontal cross-connect.

ACTION SUBMITTALS

Installation data for optical fiber cabling are specified in the referenced TIA standards.

Product Data: For each type of product.

Shop Drawings: Reviewed and stamped by RCDD.

Revise subparagraphs below to reflect District's requirements. Retain one of two "System Labeling Schedules" subparagraphs below.

System Labeling Schedules: Electronic copy of labeling schedules, in software and format selected by District.

System Labeling Schedules: Electronic copy of labeling schedules that are part of the cabling and asset identification system of the software.

Cabling administration Drawings and printouts.

Wiring diagrams and installation details of telecommunications equipment, to show location and layout of telecommunications equipment, including the following:

Telecommunications rooms plans and elevations.

Telecommunications pathways.

Telecommunications system access points.

Telecommunications grounding system.

Telecommunications conductor drop locations.

Typical telecommunications details.

Mechanical, electrical, and plumbing systems.

Fiber optic cable testing plan.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Series 01 40 ## "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For [RCDD, ] [Installer, ], installation supervisor, and field inspector.

Retain "Product Certificates" Paragraph below to require submittal of product certificates from manufacturers.

Product Certificates: For each type of product.

Source quality-control reports.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

Field quality-control reports.

CLOSEOUT SUBMITTALS

Maintenance Data: For optical fiber cable, splices, and connectors to include in maintenance manuals.

QUALITY ASSURANCE

Installer Qualifications: Cabling Installer must have personnel certified by BICSI on staff.

Layout Responsibility: Preparation of Shop Drawings[ and Cabling Administration Drawings][, Cabling Administration Drawings, and field testing program development] by an [RCDD] [Technician].

Installation Supervision: Installation shall be under the direct supervision of [Technician] [Level 2 Installer], who shall be present at all times when Work of this Section is performed at Project site.

Delete subparagraph below if Contractor performs field quality-control testing.

Testing Supervisor: Currently certified by BICSI as an [RCDD] [Technician].

Retain "Testing Agency Qualifications" Paragraph below if Contractor or manufacturer selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 01 40 00 "Quality Requirements."

Testing Agency Qualifications: Testing agency must have personnel certified by BICSI on staff.

Testing Agency's Field Supervisor: Currently certified by BICSI as an RCDD to supervise on-site testing.

DELIVERY, STORAGE, AND HANDLING

According to BICSI ITSIMM, cables should be tested upon receipt.

Test cables upon receipt at Project site.

Retain one or both of first two subparagraphs below.

Test optical fiber cable to determine the continuity of the strand end to end. Use [optical fiber flashlight] [or] [optical loss test set].

Test optical fiber cable while on reels. Use an optical time domain reflectometer to verify the cable length and locate cable defects, splices, and connector, including the loss value of each. Retain test data and include the record in maintenance data.

PROJECT CONDITIONS

Environmental Limitations: Do not deliver or install cables and connecting materials until wet work in spaces is complete and dry, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

COORDINATION

Revise this article to specify coordination with other parties involved in finalizing communications equipment room work.

Coordinate layout and installation of telecommunications pathways and cabling with District's telecommunications equipment and service suppliers.

Coordinate telecommunications outlet/connector locations with location of power receptacles at each work area.

PRODUCTS

PERFORMANCE REQUIREMENTS

General Performance: Horizontal cabling system shall comply with transmission standards in TIA-568-C.1, when tested according to test procedures of this standard.

Telecommunications Pathways and Spaces: Comply with TIA-569-D.

Grounding: Comply with TIA-607-B.

850 NANOMETER LASER-OPTIMIZED, 50/125 MICROMETER, MULTIMODE OPTICAL FIBER CABLE (OM4)

Description: Multimode, 50/125-micrometer, [1] [2] [4] -fiber, [nonconductive] [conductive, ]tight buffer, optical fiber cable.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Belden CDT Networking Division/NORDX.

Berk-Tek Leviton; a Nexans/Leviton alliance.

Commscope, Inc.

Or Equal

Standards:

Comply with ICEA S-83-596 for mechanical properties.

Comply with TIA-568-C.3 for performance specifications.

Comply with TIA-492AAAD for detailed specifications.

Maximum Attenuation:  3.50 dB/km at 850 nm; 1.5 dB/km at 1300 nm.

Minimum Overfilled Modal Bandwidth-length Product: 3500 MHz-km at 850 nm; 500 MHz-km at 1300 nm.

Minimum Effective Modal Bandwidth-length Product: 4700 MHz-km at 850 nm.

Jacket:

Jacket Color: [Aqua].

Cable cordage jacket, fiber, unit, and group color shall be according to TIA-598-D.

Imprinted with fiber count, fiber type, and aggregate length at regular intervals not to exceed 40 inches.

Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444, UL 1651, and CEC for the following types:

Plenum Rated, Nonconductive: Type OFNP, complying with NFPA 262; Type OFNP in listed plenum communications raceway; or Type OFN, Type OFNG, Type OFNP, or Type OFNR in metallic conduit.

OPTICAL FIBER CABLE HARDWARE

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Belden CDT Networking Division/NORDX.

Berk-Tek Leviton; a Nexans/Leviton alliance.

Commscope, Inc.

Or Equal.

Standards:

Comply with Fiber Optic Connector Intermateability Standard (FOCIS) specifications of the TIA-604 series.

Comply with TIA-568-C.3.

Retain "Connector Type," "Plugs and Plug Assemblies," and "Jacks and Jack Assemblies" paragraphs below to specify plugs and jacks for optical fiber cabling. "Connector Type" Paragraph applies to all products listed in this Article.

Type SC is a subscriber connector and Type ST is a straight-tip, single-fiber connector. Type LC is an upgraded version of either Type SC or Type ST with a lower insertion loss, and Type MT-RJ is a no-epoxy, no-polish connector. Type MPO allows up to 72 fibers in a single connector.

Connector Type: [Type SC complying with TIA-604-3-B,] [Type ST complying with TIA-604-2-B,] [Type LC complying with TIA-604-10-B,] [Type MT-RJ complying with TIA-604-12,] [Type MPO complying with TIA-604-5-D,] connectors.

Plugs and Plug Assemblies:

Male; color-coded modular telecommunications connector designed for termination of a single optical fiber cable.

Insertion loss not more than 0.75 dB.

Jacks and Jack Assemblies:

Female; quick-connect, simplex and duplex; fixed telecommunications connector designed for termination of a single optical fiber cable.

Insertion loss not more than 0.75 dB.

Designed to snap-in to a patch panel or faceplate.

Coordinate "Faceplate" Paragraph below with other items specified to be mounted in workstation faceplates. Revise paragraph if faceplate elevations are on Drawings.

Faceplate:

[Two][Four] [Six] -port, vertical single-gang faceplates designed to mount to single-gang wall boxes.

[Eight] [Ten] [Twelve] -port, vertical double-gang faceplates designed to mount to double-gang wall boxes.

Metal Faceplate:  Stainless steel, complying with requirements in Section 26 27 26 "Wiring Devices."

For use with snap-in jacks accommodating any combination of twisted pair, optical fiber, and coaxial work area cords.

Flush mounting jacks, positioning the cord at a 45-degree angle.

Cross-Connects and Patch Panels: Modular panels housing multiple-numbered, duplex cable connectors.

Coordinate subparagraph below with Drawings for quantity of fields.

Number of Connectors per Field:  One for each fiber of cable or cables assigned to field, plus spares and blank positions adequate to suit specified expansion criteria.

Patch Cords: Factory-made, single-fiber cables in 36-inch lengths.

Retain "Grounding" Article below if specifying conductive optical fiber cable or optical fiber cable with a shield or conductive jacket.

GROUNDING

Comply with requirements in Section 27 05 26 "Grounding and Bonding for Communications Systems" for grounding conductors and connectors.

Comply with TIA-607-B.

IDENTIFICATION PRODUCTS

Comply with TIA-606-B and UL 969 for a system of labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

SOURCE QUALITY CONTROL

Factory test multimode optical fiber cables according to TIA-526-14-B and TIA-568-C.3.

Factory test preterminated optical fiber cable assemblies according to TIA-526-14-B and TIA-568-C.3.

See Series 01 40 ## "Quality Requirements" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

Cable will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

EXECUTION

WIRING METHODS

Retain one of two "Wiring Method" paragraphs below and coordinate with Drawings. Delete both if wiring methods for system are indicated on Drawings.

Wiring Method: Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters and except in accessible ceiling spaces, in attics, and in gypsum board partitions where unenclosed wiring method may be used. Conceal raceway and cables except in unfinished spaces.

Install plenum cable in environmental air spaces, including plenum ceilings.

Comply with requirements for pathways specified in Section 27 05 28 "Pathways for Communications Systems."

Wiring Method: Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

Wiring within Enclosures: Bundle, lace, and train cables within enclosures. Connect to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools.

INSTALLATION OF OPTICAL FIBER BACKBONE CABLES

Comply with NECA 301.

General Requirements for Optical Fiber Cabling Installation:

Comply with TIA-568-C.1 and TIA-568-C.3.

Comply with BICSI ITSIMM, Ch. 6, "Cable Termination Practices."

Terminate all cables; no cable shall contain unterminated elements. Make terminations only at indicated outlets, terminals, cross-connects, and patch panels.

Cables may not be spliced. Secure and support cables at intervals not exceeding 30 inches and not more than 6 inches from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

Install lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

Bundle, lace, and train cable to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIMM, "Cabling Termination Practices" Chapter. Use lacing bars and distribution spools.

Do not install bruised, kinked, scored, deformed, or abraded cable. Do not splice cable between termination, tap, or junction points. Remove and discard cable if damaged during installation and replace it with new cable.

Cold-Weather Installation: Bring cable to room temperature before dereeling. Heat lamps shall not be used for heating.

In the communications equipment room, provide a 10-foot-long service loop on each end of cable.

Pulling Cable: Comply with BICSI ITSIMM, Ch. 4, "Pulling Cable." Monitor cable pull tensions.

Cable may be terminated on connecting hardware that is rack or cabinet mounted.

Open-Cable Installation:

Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

Cable shall not be run through structural members or in contact with pipes, ducts, or other potentially damaging items.

Group connecting hardware for cables into separate logical fields.

FIRESTOPPING

Comply with requirements in Section 07 84 13 "Penetration Firestopping."

Comply with TIA-569-D, Annex A, "Firestopping."

Comply with BICSI ITSIMM, "Firestopping" Chapter.

Retain "Grounding" Article below if specifying conductive optical fiber cable or optical fiber cable with a shield or conductive jacket.

GROUNDING

Install grounding according to BICSI ITSIMM, "Grounding (Earthing), Bonding, and Electrical Protection" Chapter.

Comply with TIA-607-B and NECA/BICSI-607.

Locate grounding bus bar to minimize the length of bonding conductors. Fasten to wall allowing at least 2-inch clearance behind the grounding bus bar. Connect grounding bus bar with a minimum No. 4 AWG grounding electrode conductor from grounding bus bar to suitable electrical building ground.

Bond metallic equipment to the grounding bus bar, using not smaller than No. 6 AWG equipment grounding conductor.

IDENTIFICATION

Identify system components, wiring, and cabling complying with TIA-606-B. Comply with requirements for identification specified in Section 27 05 53 "Identification for Communications Systems."

Administration Class:  Class 3.

Color-code cross-connect fields and apply colors to voice and data service backboards, connections, covers, and labels.

Paint and label colors for equipment identification shall comply with TIA-606-B for Class 3 level of administration including optional identification requirements of this standard.

Cable Schedule: Install in a prominent location in each equipment room and wiring closet. List incoming and outgoing cables and their designations, origins, and destinations. Protect with rigid frame and clear plastic cover. Furnish an electronic copy of final comprehensive schedules for Project.

Cabling Administration Drawings: Show building floor plans with cabling administration-point labeling. Identify labeling convention and show labels for telecommunications closets, horizontal pathways and cables, entrance pathways and cables, terminal hardware and positions, horizontal cables, work areas and workstation terminal positions, grounding buses and pathways, and equipment grounding conductors.

Cable and Wire Identification:

Label each cable within 4 inches of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

Each wire connected to building-mounted devices is not required to be numbered at device if color of wire is consistent with associated wire connected and numbered within panel or cabinet.

Exposed Cables and Cables in Cable Trays and Wire Troughs: Label each cable at intervals not exceeding 15 feet.

Label each unit and field within distribution racks and frames.

Identification within Connector Fields in Equipment Rooms and Wiring Closets: Label each connector and each discrete unit of cable-terminating and connecting hardware. Where similar jacks and plugs are used for both voice and data communication cabling, use a different color for jacks and plugs of each service.

Labels shall be preprinted or computer-printed type with printing area and font color that contrasts with cable jacket color but still complies with requirements in TIA 606-B, for the following:

Flexible vinyl or polyester that flexes as cables are bent.

FIELD QUALITY CONTROL

Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

Tests and Inspections:

Visually inspect optical fiber jacket materials for NRTL certification markings. Inspect cabling terminations in communications equipment rooms for compliance with color-coding for pin assignments, and inspect cabling connections for compliance with TIA-568-C.1.

Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

Retain subparagraph below if verification of quality is to be performed before completing horizontal cabling.

Optical Fiber Cable Tests:

Test instruments shall meet or exceed applicable requirements in TIA-568-C.1. Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

Link End-to-End Attenuation Tests:

Retain subparagraph below for multimode optical fiber cable only.

Horizontal and Multimode Horizontal Link Measurements: Test at 850 or 1300 nm in one direction according to TIA-526-14-B, Method B, One Reference Jumper.

Attenuation test results for horizontal links shall be less than 2.0 dB. Attenuation test results shall be less than those calculated according to equation in TIA-568-C.1.

Data for each measurement shall be documented. Data for submittals shall be printed in a summary report that is formatted similar to Table 10.1 in BICSI TDMM, or transferred from the instrument to the computer, saved as text files, and printed and submitted.

Remove and replace cabling where test results indicate that it does not comply with specified requirements.

See Series 01 40 ## "Quality Requirements" for retesting and reinspecting requirements and Section 01 73 00 "Execution" for requirements for correcting the Work.

End-to-end cabling will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

END OF SECTION 27 15 23

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021