MasterSpec 2010

SECTION 33 42 00

STORMWATER CONVEYANCE

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Reference Standards:

Verify design conforms to edition of reference standards cited below that is current at time of bidding.

Standard Specifications for Public Works, current edition, including Regional and City of San Diego Supplemental Amendments.

City of San Diego Standard Specifications for Public Works Construction (Whitebook), current edition.

SUMMARY

Section Includes:

Pipe and fittings.

Nonpressure transition couplings.

Cleanouts.

Drains.

Encasement for piping.

Cleanouts.

Channel drainage systems.

Catch basins.

Stormwater inlets.

Pipe outlets.

Stormwater disposal systems.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 31 20 00 "Earth Moving" for excavating, trenching, and backfilling, and underground warning tapes.

Section 33 46 00 "Subdrainage" for filter fabric.

<Insert related section(s)>.

ACTION SUBMITTALS

Product Data: For each type of product indicated.

Drop inlets.

Cleanouts and drains.

Pipe and fittings.

Shop Drawings:

Cleanouts: Include plans, elevations, sections, details, frames, and covers.

[Catch basins] [and] [stormwater inlets]. Include plans, elevations, sections, details, frames, covers, and grates.

INFORMATIONAL SUBMITTALS

Retain first paragraph below for product certificates from manufacturers.

Product Certificates:  For each type of cast-iron soil pipe and fitting, from manufacturer.

Field quality-control reports.

DELIVERY, STORAGE, AND HANDLING

Do not store plastic cleanouts, pipe, and fittings in direct sunlight.

Protect pipe, pipe fittings, and seals from dirt and damage.

Handle cleanouts according to manufacturer's written rigging instructions.

Handle [catch basins] [and] [stormwater inlets] according to manufacturer's written rigging instructions.

PROJECT CONDITIONS

Retain this article if interruption of existing storm drainage service is required.

Interruption of Existing Storm Drainage Service: Do not interrupt service to facilities occupied by District or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

Notify District Construction Manager no fewer than three days in advance of proposed interruption of service.

Do not proceed with interruption of service without District Construction Manager's written permission.

PRODUCTS

If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

HUB-AND-SPIGOT, CAST-IRON SOIL PIPE AND FITTINGS

Pipe and fittings in this article are available in NPS 2 to NPS 15 (DN 50 to DN 375).

Pipe and Fittings: ASTM A 74, Service and Extra-Heavy classes.

Gaskets: ASTM C 564, rubber.

Calking Materials: ASTM B 29, pure lead and oakum or hemp fiber.

STEEL PIPE AND FITTINGS

Piping in this article is available in NPS 4 to NPS 144 (DN 100 to DN 3600).  Standard joints with bands are soil-tight. Special joints with bands and O-rings are silt-tight.

Corrugated-Steel Pipe and Fittings: ASTM A 760/A 760M, Type I with fittings of similar form and construction as pipe.

Special-Joint Bands:  Corrugated steel with O-ring seals.

Standard-Joint Bands:  Corrugated steel.

Coating:  Zinc.

PE PIPE AND FITTINGS

Piping in first paragraph below is available in NPS 3 to NPS 10 (DN 80 to DN 250). Joints are coupling type.

Corrugated PE Drainage Pipe and Fittings NPS 3 to NPS 10: AASHTO M 252M, Type S, with smooth waterway for coupling joints.

Silt-tight Couplings: PE sleeve with ASTM D 1056, Type 2, Class A, Grade 2 gasket material that mates with tube and fittings.

Piping in paragraph below is available in NPS 12 to NPS 60 (DN 300 to DN 1500). Joints are coupling type.

Corrugated PE Pipe and Fittings NPS 12 to NPS 60: AASHTO M 294M, Type S, with smooth waterway for coupling joints.

Silt-tight Couplings: PE sleeve with ASTM D 1056, Type 2, Class A, Grade 2 gasket material that mates with pipe and fittings.

PVC PIPE AND FITTINGS

Piping in first paragraph below is available in NPS 18 to NPS 36 (DN 450 to DN 900). Joints are gasketed type. Gaskets are furnished with pipe and fittings.

PVC Gravity Sewer Piping:

Pipe and Fittings: ASTM F 679, PVC gravity sewer pipe with bell-and-spigot ends and with integral ASTM F 477, elastomeric seals for gasketed joints.

Piping in first paragraph below is available in NPS 4 to NPS 12 (DN 100 to DN 300). Joints are gasketed type.

PVC Pressure Piping:

Pipe: Pipe: ASTM D 1785, [Schedule 40] [and] [Schedule 80] PVC, with plain ends for solvent-cemented joints.

Fittings: [ASTM D 2466, Schedule 40] [and] [ASTM D 2467, Schedule 80] PVC, socket type.

CONCRETE PIPE AND FITTINGS

Reinforced-Concrete Drain Pipe and Fittings: ASTM C 76.

Bell-and-spigot or tongue-and-groove ends and gasketed joints with ASTM C 443, rubber gaskets where indicated.

NONPRESSURE TRANSITION COUPLINGS

Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition coupling, for joining underground nonpressure piping. Include ends of same sizes as piping to be joined, and corrosion-resistant-metal tension band and tightening mechanism on each end.

Sleeve Materials:

For Concrete Pipes: ASTM C 443, rubber.

For Cast-Iron Soil Pipes: ASTM C 564, rubber.

For Fiberglass Pipes: ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

For Plastic Pipes: ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

For Dissimilar Pipes: ASTM D 5926, PVC or other material compatible with pipe materials being joined.

Unshielded, Flexible Couplings:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Fernco Inc.

Mission Rubber Company.

NDS Inc.

Or Equal.

Description: Elastomeric sleeve with stainless-steel shear ring and corrosion-resistant-metal tension band and tightening mechanism on each end.

Ring-Type, Flexible Couplings:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Fernco Inc.

Logan Clay Pipe.

Mission Rubber Company.

Or Equal.

Description: Elastomeric compression seal with dimensions to fit inside bell of larger pipe and for spigot of smaller pipe to fit inside ring.

CLEANOUTS

Concrete Cleanouts:

Materials and dimensions according to City of San Diego standards.  Cleanout types and additional dimensions as indicated on Drawings.  Provide heavy duty frames and grates.

Plastic Cleanouts:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

NDS Inc.

Sioux Chief Manufacturing Company, Inc.

Zurn Industries, LLC.

Or Equal.

Description: PVC body with PVC threaded plug. Include PVC drain pipe fitting and riser to cleanout of same material as drain piping.

DRAINS

Cast-Iron Area Drains:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Smith, Jay R. Mfg. Co.

Watts; a Watts Water Technologies company.

Zurn Industries, LLC.

Or Equal.

Description: ASME A112.6.3 gray-iron round body with anchor flange and round secured grate. Include bottom outlet with inside calk or spigot connection, of sizes indicated.

Top-Loading Classification(s):  Medium and Heavy Duty.

Cast-Iron Trench Drains:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Smith, Jay R. Mfg. Co.

Watts; a Watts Water Technologies company.

Zurn Industries, LLC.

Or Equal.

Description: ASME A112.6.3, 6-inch-wide top surface, rectangular body with anchor flange or other anchoring device, and rectangular secured grate. Include units of total length indicated and quantity of bottom outlets with inside calk or spigot connections, of sizes indicated.

Top-Loading Classification(s): Medium, Heavy, and Extra-Heavy Duty.

Steel Trench Drains:

Manufacturers: Subject to compliance with requirements, provide products by the following:

Rockford Sanitary Systems, Inc.

Or Equal.

Description: Factory fabricated from ASTM A 242/A 242M, welded steel plate, to form rectangular body with uniform bottom downward slope of 2 percent toward outlet, anchor flange, and grate. Include units of total length indicated, bottom outlet of size indicated, outlet strainer, acid-resistant enamel coating on inside and outside surfaces, and grate with openings of total free area at least two times cross-sectional area of outlet.

Plate Thicknesses:  1/8-inch and 1/4-inch.

Overall Widths:  7-1/2 inches and 12-1/3 inches.

Grate Openings:  3/8-inch circular or 3/8-by-3-inch slots.

ENCASEMENT FOR PIPING

Standard: ASTM A 674 or AWWA C105.

Material: [Linear low-density polyethylene film of 0.008-inch] [or] [high-density, cross-laminated polyethylene film of 0.004-inch] minimum thickness.

Form: [Sheet] [or] [tube].

Color: [Black] [or] [natural].

POLYMER-CONCRETE, CHANNEL DRAINAGE SYSTEMS

General Requirements for Polymer-Concrete, Channel Drainage Systems: Modular system of precast, polymer-concrete channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling. Include quantity of units required to form total lengths indicated.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ACO USA.

Innovative Plastic, Inc.

Polycast: Hubbell Power Systems, Inc.

Or Equal.

Retain one of first three paragraphs below.

Sloped-Invert, Polymer-Concrete Systems:

Channel Sections:

Interlocking-joint, precast, modular units with end caps.

4-inch inside width and deep, rounded bottom, with built-in invert slope of 0.6 percent and with outlets in quantities, sizes, and locations indicated.

Extension sections necessary for required depth.

Frame: Include gray-iron or steel frame for grate.

Grates:

Manufacturer's designation "[Heavy] [Medium] Duty," with slots or perforations that fit recesses in channels.

Material: [Fiberglass] [or] [Gray iron].

Covers: Solid gray iron if indicated.

Locking Mechanism: Manufacturer's standard device for securing grates to channel sections.

Narrow-Width, Level-Invert, Polymer-Concrete Systems:

Channel Sections:

Interlocking-joint, precast, modular units with end caps.

5-inch inside width and 9-3/4-inch-deep, rounded bottom, with level invert and with NPS 4 outlets in quantities, sizes, and locations indicated.

Grates:

Slots or perforations that fit recesses in channels.

Material:  [Fiberglass] [or] [Gray iron].

Covers: Solid gray iron if indicated.

Locking Mechanism: Manufacturer's standard device for securing grates to channel sections.

Wide-Width, Level-Invert, Polymer-Concrete Systems:

Channel Sections:

Interlocking-joint, precast, modular units with end caps.

8-inch inside width and 13-3/4-inch-deep, rounded bottom, with level invert and with outlets in quantities, sizes, and locations indicated.

Grates:

Slots or other openings that fit recesses in channels.

Material: [Fiberglass] [or] [Gray iron].

Covers:  Solid gray iron if indicated.

Locking Mechanism: Manufacturer's standard device for securing grates to channel sections.

Drainage Specialties: Precast, polymer-concrete units.

Revise four subparagraphs below to suit Project.

Large Catch Basins:

24-by-12-inch polymer-concrete body, with outlets in quantities and sizes indicated.

Gray-iron slotted grate.

Frame: Include gray-iron or steel frame for grate.

Small Catch Basins:

19- to 24-inch by approximately 6-inch polymer-concrete body, with outlets in quantities and sizes indicated.

Gray-iron slotted grate.

Frame: Include gray-iron or steel frame for grate.

Oil Interceptors:

Polymer-concrete body with interior baffle and four steel support channels and two 1/4-inch-thick, steel-plate covers.

Steel-plate covers.

Capacity:  As indicated on drawings.

Inlet and Outlet:  As indicated on drawings.

Sediment Interceptors:

27-inch-square, polymer-concrete body, with outlets in quantities and sizes indicated.

24-inch-square, gray-iron frame and slotted grate.

Supports, Anchors, and Setting Devices: Manufacturer's standard unless otherwise indicated.

Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

PLASTIC, CHANNEL DRAINAGE SYSTEMS

Retain systems in this article for light traffic areas. Delete article if entire system is heavy-duty construction.

General Requirements for Plastic, Channel Drainage Systems:

Modular system of plastic channel sections, grates, and appurtenances.

Designed so grates fit into frames without rocking or rattling.

Number of units required to form total lengths indicated.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

ACO USA.

NDS Inc.

Zurn Industries, LLC.

Or Equal.

Fiberglass Systems:

Channel Sections:

Interlocking-joint, fiberglass modular units, with built-in invert slope of approximately 1 percent and with end caps.

Rounded or inclined inside bottom surface, with outlets in quantities, sizes, and locations indicated.

Width:  6 or 8 inches.

Factory- or field-attached frames that fit channel sections and grates.

Material:  Manufacturer's standard metal.

Grates with slots or perforations that fit frames.

Material: [Fiberglass] [or] [Gray iron].

Covers: Solid gray iron if indicated.

Drainage Specialties:

Large Catch Basins: 24-inch-square plastic body, with outlets in quantities and sizes indicated. Include gray-iron frame and slotted grate.

Small Catch Basins: 12-by-24-inch plastic body, with outlets in quantities and sizes indicated. Include gray-iron frame and slotted grate.

PE Systems:

Channel Sections: Interlocking-joint, PE modular units, 4 inches wide, with end caps. Include rounded bottom, with level invert and with outlets in quantities, sizes, and locations indicated.

Grates: PE, ladder shaped; with stainless-steel screws.

Color: Gray unless otherwise indicated.

Drainage Specialties: Include the following PE components:

Retain one of five subparagraphs below.

Drains: 4-inch-diameter, round, slotted top; with NPS 4 bottom outlet.

Drains: 8-inch-diameter, round, slotted top; with NPS 6 bottom outlet.

Drains: 4-inch-square, slotted top; with NPS 3 bottom outlet.

Drains: 8-inch-square, slotted top; with NPS 6 bottom outlet.

Catch Basins: 12-inch-square plastic body, with outlets in quantities and sizes indicated. Include PE slotted grate 11-3/4 inches square by 1-1/8 inches thick.

Supports, Anchors, and Setting Devices:  Manufacturer's standard unless otherwise indicated.

Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

CATCH BASINS

Standard Precast Concrete Catch Basins:

Materials and dimensions per City of San Diego standards.

Type of catch basin and additional dimensions as indicated on Drawings.

STORMWATER INLETS

Curb Inlets:  Made with vertical curb opening, of materials and dimensions according to City of San Diego standards.

Gutter Inlets: Made with horizontal gutter opening, of materials and dimensions according to City of San Diego standards. Include heavy-duty frames and grates.

Combination Inlets: Made with vertical curb and horizontal gutter openings, of materials and dimensions according to City of San Diego standards. Include heavy-duty frames and grates.

Frames and Grates: Heavy duty, according to City of San Diego standards.

PIPE OUTLETS

Riprap Basins:  Broken, irregularly sized and shaped, graded stone according to NSSGA's "Quarried Stone for Erosion and Sediment Control."

Average Size:  As indicated on drawings.

Filter Stone: According to NSSGA's "Quarried Stone for Erosion and Sediment Control," No. FS-2, No. 4 screen opening, average-size graded stone.

STORMWATER DISPOSAL SYSTEMS

Retain one of two paragraphs below.

Chamber Systems:

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Advanced Drainage Systems, Inc.

CULTEC, Inc.

Hancor Inc.

Or Equal.

Storage and Leaching Chambers: Molded PE with perforated sides and open bottom. Include number of chambers, distribution piping, end plates, and other standard components as required for system total capacity.

Filtering Material: ASTM D 448, Size No. 24, 3/4- to 2-1/2-inch washed, crushed stone or gravel unless shown otherwise.

Filter Mat: Geotextile woven or spun filter fabric, in one or more layers, for minimum total unit weight of 4 oz./sq. yd..

Pipe Systems: Perforated manifold, header, and lateral piping complying with AASHTO M 252M for NPS 10 and smaller, AASHTO M 294M for NPS 12 to NPS 60. Include proprietary fittings, couplings, seals, and filter fabric.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Advanced Drainage Systems, Inc.

Hancor Inc.

Or Equal.

EXECUTION

PIPING INSTALLATION

General Locations and Arrangements: Drawing plans and details indicate general location and arrangement of underground storm drainage piping. Location and arrangement of piping layout take into account design considerations. Install piping as indicated, to extent practical. Where specific installation is not indicated, follow piping manufacturer's written instructions.

Install piping beginning at low point, true to grades and alignment indicated with unbroken continuity of invert. Place bell ends of piping facing upstream. Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements.

Install cleanouts for changes in direction unless fittings are indicated. Use fittings for branch connections unless direct tap into existing drain is indicated.

Install proper size increasers, reducers, and couplings where different sizes or materials of pipes and fittings are connected.  Reducing size of piping in direction of flow is prohibited.

When installing pipe under streets or other obstructions that cannot be disturbed, use pipe-jacking process of microtunneling.

Install gravity-flow, nonpressure drainage piping according to the following:

Install piping pitched down in direction of flow.

Install piping [NPS 6] and larger with restrained joints at tee fittings and at changes in direction. Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place concrete supports or anchors.

Install piping with 36-inch minimum cover unless drawings indicate otherwise.

Install hub-and-spigot, cast-iron soil piping according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook."

Install corrugated steel piping according to ASTM A 798/A 798M.

Install PE corrugated drain piping according to the following:

Encase in Type C rock envelope according to City of San Diego Standard Drawing SDS110.  Surround crushed rock with filter fabric.

Pipe with less than 2 feet of cover: Encase in concrete according to Regional Standard Drawing S-7.

Backfill trench and compact.

Install PVC drain piping according to ASTM D 2321 and ASTM F 1668.

Install concrete drain piping according to ASTM C 1479 and ACPA's "Concrete Pipe Installation Manual."

Install force-main pressure piping according to the following:

Install piping with restrained joints at tee fittings and at horizontal and vertical changes in direction. Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place concrete supports or anchors.

Install piping with 36-inch minimum cover unless drawings indicate otherwise.

Install PVC pressure piping according to AWWA M23, or ASTM D 2774 and ASTM F 1668.

Install corrosion-protection as indicated on drawings.

PIPE JOINT CONSTRUCTION

Join gravity-flow, nonpressure drainage piping according to the following:

Join hub-and-spigot, cast-iron soil piping with gasketed joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for compression joints.

Join hub-and-spigot, cast-iron soil piping with calked joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for lead and oakum calked joints.

Join corrugated steel drain piping according to ASTM A 798/A 798M.

Join corrugated PE piping according to ASTM D 3212 for push-on joints.

Join PVC profile gravity drain piping according to ASTM D 2321 for elastomeric-seal joints or ASTM F 794 for gasketed joints.

Join concrete drain piping according to ASTM C 14 and ACPA's "Concrete Pipe Installation Manual" for rubber-gasketed joints.

Join dissimilar pipe materials with nonpressure-type flexible couplings.

Join force-main pressure piping according to the following:

Join PVC pressure piping according to ASTM D 2855 for solvent-cemented joints.

Join dissimilar pipe materials with pressure-type couplings.

CLEANOUT INSTALLATION

Concrete Cleanouts: Construct concrete cleanouts according to City of San Diego standards.  Set cleanout frames and covers flush with finished surface.

Plastic Cleanouts:  Use cast-iron soil pipe fittings in drain pipes at branches for cleanouts and cast-iron soil pipe for riser extensions to cleanouts. Install piping so cleanouts open in direction of flow in drain pipe.

Install cleanouts and riser extensions from drain pipes to cleanouts at grade.

Use commercially manufactured 45 degree wye and 45 degree bend fittings in storm drain pipes and risers for cleanouts.

Install piping so cleanouts open in direction of flow in storm drain pipe.

Unpaved Areas: Set cleanout tops 1-inch above surrounding earth grade.

Paved Areas (Walkways, Roadways, etc.): Set cleanout tops flush with pavement surface.

DRAIN INSTALLATION

Install type of drains in locations indicated.

Use Light-Duty, top-loading classification drains in earth or unpaved foot-traffic areas.

Use Medium-Duty, top-loading classification drains in paved foot-traffic areas.

Use Heavy-Duty, top-loading classification drains in vehicle-traffic service and parking areas.

Use Extra-Heavy-Duty, top-loading classification drains in roads.

Embed drains in 4-inch minimum concrete around bottom and sides.

Fasten grates to drains if indicated.

Set drain frames and covers with tops flush with pavement surface.

Assemble trench sections with flanged joints.

Embed trench sections in 4-inch minimum concrete around bottom and sides.

CATCH BASIN INSTALLATION

Construct in accordance with City of San Diego standards.

Construct to sizes and shapes indicated on Drawings

Set frames and grates to elevations indicated.

STORMWATER INLET AND OUTLET INSTALLATION

Construct inlet head walls, aprons, and sides of reinforced concrete, as indicated.

Construct riprap of broken stone, as indicated.

Install outlets that spill onto grade, anchored with concrete, where indicated.

Install outlets that spill onto grade, with flared end sections that match pipe, where indicated.

Construct energy dissipaters at outlets, as indicated.

CONCRETE PLACEMENT

Place cast-in-place concrete according to ACI 318.

CHANNEL DRAINAGE SYSTEM INSTALLATION

Install with top surfaces of components, except piping, flush with finished surface.

Assemble channel sections to form slope down toward drain outlets. Use sealants, adhesives, fasteners, and other materials recommended by system manufacturer.

Embed channel sections and drainage specialties in 4-inch minimum concrete around bottom and sides.

Fasten grates to channel sections if indicated.

Assemble channel sections with flanged or interlocking joints.

Embed channel sections in 4-inch minimum concrete around bottom and sides.

STORMWATER DISPOSAL SYSTEM INSTALLATION

Retain one of two paragraphs below to match systems specified.

Chamber Systems: Excavate trenches of width and depth, and install system and backfill according to chamber manufacturer's written instructions. Include storage and leaching chambers, filtering material, and filter mat.

Piping Systems: Excavate trenches of width and depth, and install piping system, filter fabric, and backfill, according to piping manufacturer's written instructions.

CONNECTIONS

Connect nonpressure, gravity-flow drainage piping in building's storm building drains.

Connect force-main piping to building's storm drainage force mains.

Make connections to existing piping and underground manholes or cleanouts.

Use commercially manufactured wye fittings for piping branch connections. Remove section of existing pipe; install wye fitting into existing piping; and encase entire wye fitting, plus 6-inch overlap, with not less than 6 inches of concrete with 28-day compressive strength of 3000 psi.

Make branch connections from side into existing piping, NPS 4 to NPS 20. Remove section of existing pipe, install wye fitting into existing piping, and encase entire wye with not less than 6 inches of concrete with 28-day compressive strength of 3000 psi.

Make branch connections from side into existing piping, NPS 21 or larger, or to underground manholes, cleanouts, and structures by cutting into existing unit and creating an opening large enough to allow 3 inches of concrete to be packed around entering connection. Cut end of connection pipe passing through pipe or structure wall to conform to shape of and be flush with inside wall unless otherwise indicated. On outside of pipe, manhole, cleanout, or structure wall, encase entering connection in 6 inches of concrete for minimum length of 12 inches to provide additional support of collar from connection to undisturbed ground.

Use concrete that will attain a minimum 28-day compressive strength of 3000 psi unless otherwise indicated.

Use epoxy-bonding compound as interface between new and existing concrete and piping materials.

Protect existing piping, manholes, cleanouts, and structures to prevent concrete or debris from entering while making tap connections. Remove debris or other extraneous material that may accumulate.

Pipe couplings, expansion joints, and deflection fittings with pressure ratings at least equal to piping rating may be used in applications below unless otherwise indicated.

Use nonpressure-type flexible couplings where required to join gravity-flow, nonpressure drain piping unless otherwise indicated.

Shielded flexible couplings for same or minor difference OD pipes.

Unshielded, increaser/reducer-pattern, flexible couplings for pipes with different OD.

Ring-type flexible couplings for piping of different sizes where annular space between smaller piping's OD and larger piping's ID permits installation.

Use pressure-type pipe couplings for force-main joints.

CLOSING ABANDONED STORM DRAINAGE SYSTEMS

Abandoned Piping: Close open ends of abandoned underground piping indicated to remain in place. Include closures strong enough to withstand hydrostatic and earth pressures that may result after ends of abandoned piping have been closed. Use either procedure below:

Close open ends of piping with at least 8-inch-thick, brick masonry bulkheads.

Close open ends of piping with threaded metal caps, plastic plugs, or other acceptable methods suitable for size and type of material being closed. Do not use wood plugs.

Abandoned Manholes, Cleanouts, and Structures: Excavate around manholes, cleanouts, and structures as required and use one procedure below:

Remove manhole, cleanout, or structure and close open ends of remaining piping.

Remove top of manhole, cleanout, or structure down to at least 36 inches below final grade. Fill to within 12 inches of top with stone, rubble, gravel, or compacted dirt. Fill to top with concrete.

Backfill to grade.

IDENTIFICATION

Arrange for installation of green warning tape directly over piping and at outside edge of underground structures.

Use warning tape or detectable warning tape over ferrous piping.

Use detectable warning tape over nonferrous piping and over edges of underground structures.

FIELD QUALITY CONTROL

Inspect interior of piping to determine whether line displacement or other damage has occurred. Inspect after approximately 24 inches of backfill is in place, and again at completion of Project.

Submit separate reports for each system inspection.

Defects requiring correction include the following:

Alignment: Less than full diameter of inside of pipe is visible between structures.

Deflection: Flexible piping with deflection that prevents passage of ball or cylinder of size not less than 92.5 percent of piping diameter.

Damage: Crushed, broken, cracked, or otherwise damaged piping.

Infiltration: Water leakage into piping.

Exfiltration: Water leakage from or around piping.

Replace defective piping using new materials, and repeat inspections until defects are within allowances specified.

Reinspect and repeat procedure until results are satisfactory.

Test new piping systems, and parts of existing systems that have been altered, extended, or repaired, for leaks and defects.

Do not enclose, cover, or put into service before inspection and approval.

Test completed piping systems according to requirements of authorities having jurisdiction.

Schedule tests and inspections by authorities having jurisdiction with at least 24 hours' advance notice.

Submit separate report for each test.

Gravity-Flow Storm Drainage Piping: Test according to requirements of authorities having jurisdiction, UNI-B-6, and the following:

Exception: Piping with soil-tight joints unless required by authorities having jurisdiction.

Option: Test plastic piping according to ASTM F 1417.

Option: Test concrete piping according to ASTM C 924.

Leaks and loss in test pressure constitute defects that must be repaired.

Replace leaking piping using new materials, and repeat testing until leakage is within allowances specified.

CLEANING

Clean interior of piping of dirt and superfluous materials.  Flush with potable water.

END OF SECTION 33 42 00

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021