MasterSpec 2010

SECTION 33 46 00

SUBDRAINAGE

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

MANDATORY REQUIREMENT:  Retain this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Related Requirements

Section 32 92 00 "Turf and Grasses" for placing planting soil for turf and grasses.

SUMMARY

Section Includes:

Perforated-wall pipe and fittings.

Drainage panels.

Geotextile filter fabrics.

ACTION SUBMITTALS

Product Data:

Drainage conduits, including rated capacities.

Drainage panels, including rated capacities.

Geotextile filter fabrics.

COORDINATION

Coordinate foundation drainage system installation with excavating, trenching, and backfilling.

Coordinate drainage panel installation with waterproofing of walls below grade.

Coordinate piping termination with storm drainage system.

PRODUCTS

PERFORATED-WALL PIPES AND FITTINGS

General:  Include pipes, fittings, couplings, and joint materials.

Perforated PVC Sewer Pipe and Fittings: ASTM D 2729, bell-and-spigot ends, for loose joints.

Retain “Molded-Sheet Drainage Panel" Article below if required, usually for foundation walls. Delete if drainage panels are specified in Section 07 13 26 "Self-Adhering Sheet Waterproofing”.

MOLDED-SHEET DRAINAGE PANELS

Description:  Prefabricated composite drainage panels, made with drainage core and faced with filter fabric, for use as part of foundation drainage system.

: Subject to compliance with requirements, provide products by the following:

Carlisle Coatings & Waterproofing, Inc..

Grace Construction Products; W.R. Grace & Co.

Polyguard Products, Inc.

Or Equal.

Drainage Core: Three-dimensional, non-biodegradable, molded-plastic-sheet material designed to effectively conduct water to foundation drainage system under maximum soil pressures.

Flow Rate:  9 to 15 gpm/ft. at hydraulic gradient of 1.0 and 3600 psf normal pressure when tested according to ASTM D 4716.

Minimum Compressive Strength: 18,000 lbf/sq.ft.

Filter Fabric:  Nonwoven needle-punched geotextile, manufactured for subsurface drainage, made from polyolefins or polyesters; with elongation greater than 50 percent; complying with the following properties determined according to AASHTO M 288:

Survivability:  [Class 1] [Class 2] [Class 3].

Apparent Opening Size: [No. 30] [No. 40] [No. 60][No. 70] [No. 80] sieve, maximum.

Permittivity:  [0.5] [0.2] [0.1] per second, minimum.

SOIL MATERIALS

Soil materials are specified in Section 31 20 00 "Earth Moving."

WATERPROOFING FELTS

Material: Comply with ASTM D 226, Type I, asphalt-saturated organic felt.

GEOTEXTILE FILTER FABRICS

Description:  Fabric of polypropylene (PP) or polyester fibers or combination of both, with flow rate range from 110 to 330 gpm/sq. ft. when tested according to ASTM D 4491.

Structure Type:  Nonwoven, needle-punched continuous filament.

Survivability:  AASHTO M 288 Class 2.

Styles:  Flat and sock.

EXECUTION

EXAMINATION

Examine surfaces and areas for suitable conditions where subdrainage systems are to be installed.

Retain first paragraph below if subdrainage system is required for landscaped areas.

If subdrainage is required for landscaping, locate and mark existing utilities, underground structures, and aboveground obstructions before beginning installation and avoid disruption and damage of services.

Verify that drainage panels installed as part of foundation wall waterproofing is properly positioned to drain into subdrainage system.

Proceed with installation only after unsatisfactory conditions have been corrected.

EARTHWORK

Excavating, trenching, and backfilling are specified in Section 31 20 00 "Earth Moving."

FOUNDATION DRAINAGE INSTALLATION

Place impervious fill material on subgrade adjacent to bottom of footing after concrete footing forms have been removed. Place and compact impervious fill to dimensions indicated, but not less than 6 inches deep and 12 inches wide.

Lay flat-style geotextile filter fabric in trench and overlap trench sides.

Place supporting layer of drainage course over compacted subgrade and geotextile filter fabric, to compacted depth of not less than 4 inches.

Install drainage piping as indicated in Part 3 "Piping Installation" Article for foundation subdrainage.

Add drainage course to width of at least 6 inches on side away from wall and to top of pipe to perform tests.

After satisfactory testing, cover drainage piping to width of at least 6 inches on side away from footing and above top of pipe to within 12 inches of finish grade.

Install drainage course and wrap top of drainage course with flat-style geotextile filter fabric.

Place layer of geotextile filter fabric over top of drainage course, overlapping edges at least 4 inches.

Install drainage panels on foundation walls as follows:

Coordinate placement with other drainage materials.

Comply with manufacturer's written instructions for securing drainage panels to substrate.  Use adhesives and mechanical fasteners recommended by manufacturer.  Lap edges of fabric and extend fabric around foundation drainage pipe according to manufacturer's recommendations.  Do not penetrate waterproofing.  Protect installed panels during backfilling

Lay perforated drainage pipe at base of footing. Install as indicated in Part 3 "Piping Installation" Article.

Separate 4 inches of fabric at beginning of roll and cut away 4 inches of core. Wrap fabric around end of remaining core.

Attach panels to wall beginning at subdrainage pipe. Place and secure molded-sheet drainage panels, with geotextile facing away from wall.

Place backfill material over compacted drainage course. Place material in loose-depth layers not exceeding 6 inches. Thoroughly compact each layer. Final backfill to finish elevations and slope away from building.

UNDERSLAB DRAINAGE INSTALLATION

Excavate for underslab drainage system after subgrade material has been compacted but before drainage course has been placed. Include horizontal distance of at least 6 inches between drainage pipe and trench walls. Grade bottom of trench excavations to required slope, and compact to firm, solid bed for drainage system.

Lay flat-style geotextile filter fabric in trench and overlap trench sides.

Place supporting layer of drainage course over compacted subgrade and geotextile filter fabric, to compacted depth of not less than 4 inches.

Install drainage piping as indicated in Part 3 "Piping Installation" Article for underslab subdrainage.

Add drainage course to width of at least 6 inches on side away from wall and to top of pipe to perform tests.

After satisfactory testing, cover drainage piping with drainage course to elevation of bottom of slab, and compact and wrap top of drainage course with flat-style geotextile filter fabric.

Install horizontal drainage panels as follows:

Coordinate placement with other drainage materials.

Lay perforated drainage pipe at inside edge of footing.

Place drainage panel over drainage pipe with core side up. Peel back fabric and wrap fabric around pipe. Locate top of core at bottom elevation of floor slab.

Butt additional panels against other installed panels. If panels have plastic flanges, overlap installed panel with flange.

RETAINING-WALL DRAINAGE INSTALLATION

Retain one of first two paragraphs below.

Lay flat-style geotextile filter fabric in trench and overlap trench sides.

Place supporting layer of drainage course over compacted subgrade to compacted depth of not less than 4 inches.

Install drainage piping as indicated in Part 3 "Piping Installation" Article for retaining-wall subdrainage.

Add drainage course to width of at least 6 inches on side away from wall and to top of pipe to perform tests.

After satisfactory testing, cover drainage piping to width of at least 6 inches on side away from footing and above top of pipe to within 12 inches of finish grade.

Place drainage course in layers not exceeding 3 inches in loose depth; compact each layer placed and wrap top of drainage course with flat-style geotextile filter fabric.

Place layer of flat-style geotextile filter fabric over top of drainage course, overlapping edges at least 4 inches.

Install drainage panels on wall as follows:

Coordinate placement with other drainage materials.

Comply with manufacturer's written instructions for securing drainage panels to substrate.  Use adhesives and mechanical fasteners recommended by manufacturer.  Lap edges of fabric and extend fabric around foundation drainage pipe according to manufacturer's recommendations.  Do not penetrate waterproofing.  Protect installed panels during backfilling.

Lay perforated drainage pipe at base of footing as described elsewhere in this Specification. Do not install aggregate.

If weep holes are indicated instead of drainage pipe, cut 1/2-inch-diameter holes on core side at weep-hole locations. Do not cut fabric.

Cut panel as necessary to keep top 12 inches below finish grade.

For inside corners, bend panel. For outside corners, cut core to provide 3 inches for overlap.

Fill to Grade: Place satisfactory soil fill material over compacted drainage course. Place material in loose-depth layers not exceeding 6 inches. Thoroughly compact each layer.  Fill to finish grade.

LANDSCAPING DRAINAGE INSTALLATION

Provide trench width to allow installation of drainage conduit. Grade bottom of trench excavations to required slope, and compact to firm, solid bed for drainage system.

Lay flat-style geotextile filter fabric in trench and overlap trench sides.

Place supporting layer of drainage course over compacted subgrade and geotextile filter fabric, to compacted depth of not less than 4 inches.

Install drainage conduits as indicated in Part 3 "Piping Installation" Article for landscaping subdrainage with horizontal distance of at least 6 inches between conduit and trench walls. Wrap drainage conduits without integral geotextile filter fabric with flat-style geotextile filter fabric before installation. Connect fabric sections with adhesive or tape.

Add drainage course to top of drainage conduits.

After satisfactory testing, cover drainage conduit to within 12 inches of finish grade.

Install drainage course and wrap top of drainage course with flat-style geotextile filter fabric.

Place layer of flat-style geotextile filter fabric over top of drainage course, overlapping edges at least 4 inches.

Fill to Grade: Place satisfactory soil fill material over drainage course. Place material in loose-depth layers not exceeding 6 inches. Thoroughly compact each layer. Fill to finish grade.

PIPING INSTALLATION

Drawings indicate general location and arrangement of foundation drainage system piping.

Install piping beginning at low points of system, true to grades and alignment indicated, with unbroken continuity of invert. Bed piping with full bearing in filtering material. Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions and other requirements indicated.

Of first four subparagraphs below, retain only those applicable to Project.

Foundation and Retaining Wall Subdrainage:  Install piping pitched down, at a minimum of 1 percent unless otherwise indicated.

Underslab Subdrainage:  Install piping level.

Plaza Deck Subdrainage:  Install piping level.

Landscaping Subdrainage:  Install piping pitched down in direction of flow, at a minimum slope of 0.5 percent unless otherwise indicated.

Lay perforated pipe with perforations down.

Revise subparagraph below to suit Project or delete.

Excavate recesses in trench bottom for bell ends of pipe. Lay pipe with bells facing upslope and with spigot end entered fully into adjacent bell.

Use increasers, reducers, and couplings made for different sizes or materials of pipes and fittings being connected.  Reduction of pipe size in direction of flow is prohibited.

Extend piping and connect to storm drainage system or daylight as indicated.

PIPE JOINT CONSTRUCTION

Join perforated PVC sewer pipe and fittings according to ASTM D 3212 with loose bell-and-spigot, push-on joints.

Special Pipe Couplings: Join piping made of different materials and dimensions with special couplings made for this application. Use couplings that are compatible with and fit materials and dimensions of both pipes.

CLEANOUT INSTALLATION

Comply with requirements for cleanouts specified in Section 33 42 00 "Stormwater Conveyance."

Cleanouts for Subdrainage:

Install cleanouts from piping to grade. Locate cleanouts at beginning of piping run and at changes in direction. Install fittings so cleanouts open in direction of flow in piping.

In vehicular-traffic areas, unless indicated otherwise, use NPS 4 cast-iron soil pipe and fittings for piping branch fittings and riser extensions to cleanout. Set cleanout frames and covers in a cast-in-place concrete anchor, 18-by-18-by-12 inches deep. Set top of cleanout flush with grade.

In nonvehicular-traffic areas, use NPS 4 PVC pipe and fittings for piping branch fittings and riser extensions to cleanout. Set cleanout frames and covers in a cast-in-place concrete anchor, 12-by-12-by-4 inches deep. Set top of cleanout 1 inch above grade.

Comply with requirements for concrete specified in Section 03 30 00 "Cast-in-Place Concrete."

Cleanouts for Underslab Subdrainage:

Install cleanouts and riser extensions from piping to top of slab. Locate cleanouts at beginning of piping run and at changes in direction. Install fittings so cleanouts open in direction of flow in piping.

Use NPS 4 cast-iron soil pipe and fittings for piping branch fittings and riser extensions to cleanout flush with top of slab.

CONNECTIONS

Comply with requirements for piping specified in Section 33 42 00 "Stormwater Conveyance."  Drawings indicate general arrangement of piping, fittings, and specialties.

Retain option in first paragraph below if connection will be to building's storm drainage system.

Unless otherwise indicated, connect low elevations of subdrainage system to building's solid-wall-piping storm drainage system.

Where required, connect low elevations of subdrainage to stormwater sump pumps. Comply with requirements for sump pumps specified in Section 22 14 29 "Sump Pumps."

FIELD QUALITY CONTROL

Retain first paragraph below to describe tests and inspections to be performed. Insert specific test requirements to comply with authorities having jurisdiction.

Tests and Inspections:

After installing drainage course to top of piping, test drain piping with water to ensure free flow before backfilling.

Remove obstructions, replace damaged components, and repeat test until results are satisfactory.

Drain piping will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

CLEANING

Clear interior of installed piping and structures of dirt and other superfluous material as work progresses. Maintain swab or drag in piping and pull past each joint as it is completed. Place plugs in ends of uncompleted pipe at end of each day or when work stops.

END OF SECTION 33 46 00

Retain this notice in all Sections of Project Manual.

San Diego Unified School District Guide Specifications

Document Version: August 2021